L&G Meter Firmware S00244-08.02.R64 and S00261-08.02.R64

Test Summary Report

Meter FW Upgrade  Project

Document Control

| Version No: | 1.0 |
| --- | --- |
| Created On: | 24 October 2024 |
| Last Updated: | 14 January 2024 |
| Status: | Final |
| Author/s: | Manoj Kalra |

Approval Status

| Stakeholder Role | Stakeholder Name | Signature | Date |
| --- | --- | --- | --- |
| Head of Network Intelligence | Tobie DeVilliers |  |  |
| Communication Networks Manager | Stuart Bannister |  |  |
| Metering Asset Manager | Goutham Lingam |  | 01-April-2025 |
| IOT Systems Service Lead | Wilton Gao |  | 02-April-2025 |
| Market & Meter Data Manager | Jack Friel |  | 01-April-2025 |
| Manager Communication Networks Quality | Leonard Jarillas |  | 15-April-2025 |

Document Purpose

The purpose of the Test Summary Report is to record the results of testing for the Meter Firmware 08.02.R64 (S00244-08.02.R64 and S00261-08.02.R64).  This document will provide a synopsis of the testing planned, any variations to this plan and details of the results. The reference for these FW testing is the Firmware release notes attached in the section 10.1.

Included in this document is an overview of Defects, providing Stakeholders  with a view of the issues raised during testing and actions for any unresolved  defects at the time the testing was completed.  This document will be used as an approval point prior to Deployment.

Related Documents

This section will list related documents. Please note that if this document is updated these related documents may also need to be changed.

| Document | Location | Relationship |
| --- | --- | --- |
| E350 U1300 FW Internal Release Notes S00244-08.02.004.pdf | Appendix: 10.1 Firmware Release Notes | Scope |
| E350 U3400 Release Notes 8.2.008 v1.pdf | Appendix: 10.1 Firmware Release Notes | Scope |

Reviewers

List the relevant reviewers who are responsible for the deliverables defined in this document.

| Reviewer | Name | Comments/Approval |
| --- | --- | --- |
| UIQ Systems Analyst | Nelson Manio |  |
| IoT Systems Administrator | Amy Fan |  |
| Senior Metering Engineer | Fabian Perez |  |
| Compliance & Projects Analyst | Wayne Johnson | Reviewed |
| Market & Meter Data Team Leader | Karen Krizmanic |  |
| Market & Meter Data Team Leader | Can Turk |  |
| AMI Communications Control Operator | Percy Arachchige | Reviewed |
| AMI Communications Analyst | Wayne Sangsukdee | Reviewed |
| AMI Communications Analyst | Jogy Cherian | Reviewed |

Contents

1.	Introduction	4

2.	Deviations from Test Plan	4

3.	Summary of Test Activity	4

4.	Test Coverage	4

4.1.	Meter Firmware 08.02.R64 – U1300 and U3400	4

5.	Exit Criteria	6

6.	Test Execution Summary	7

6.1.	08.02.R64 meter firmware	7

6.2.	Exceptions	7

7.	Defect Summary	8

7.1.	Accepted Defects	8

7.2.	Deferred Defects	8

7.3.	Fix by Project Closure	9

7.3.1.	Open Defects	9

8.	Identified Risks	9

9.	Location of defects and test results	10

9.1.	Location of Tests	10

10.	Appendix	11

10.1.	Firmware Release Notes	11

10.2.	Test results	11

10.2.1.	Overall Test Case Results and Defects.	11

10.2.2.	Exceptions	11

10.3.	Meter FW 08.02.R64 Defects Workarounds	11

10.4.	Deployment Notes	11

10.4.1.	Meter FW upgrade from R54/R59 to 08.02.R64	11

10.4.2.	Meter FW upgrade during Priority Override in progress	12

10.4.3.	Boost primacy on upgraded meters	12

10.4.4.	Meter Program export XML file	12

11.	Result and Recommendation	12

12.	Definitions and Acronyms	12

13.	Revision	13

# Introduction

There is new meter firmware 08.02.R64 released from L&G for U1300 and U3400 meters.  This firmware will be used to upgrade the production meters. This Firmware resloves some of the existing issues in previous released firmware. E.g

- Upgrade to R59 (8.1.14) is corrupting the meter program and meter data on U-Series meters

- U3400/U1300 - FW-Load Control command -1 when issued from UIQ system is not working with R5.9 FW

The purpose of the Test Summary Report is to record the results of testing of the 08.02.R64 meter firmware VPN meters under UIQ v5.  This document will provide a synopsis of the firmware covered and details of the results.

Included in this document is an overview of Defects, providing Stakeholders with a view of the issues raised during testing and actions for any unresolved defects or outstanding test items.  This document will be used as an approval point prior to deploy to production.

# Deviations from Test Plan

Not Applicable As there were no Test Plan document was created for this testing activity. There were predefined test set that were used to perform the testing for new Meter FW.

# Summary of Test Activity

Testing for Firmware S00261-08.02.R64 and S00244-08.02.R64 was completed on 18/10/2024 Testing was mainly conducted in the UIQ DEV (VPN) environments.

Summarising the testing:

- 362 test cases were initially assigned for execution during these testing activities.

  - During execution 12 test cases were marked as not applicable.

  - 2 test cases were marked as Blocked.

  - 223 test cases had passed and 22 test cases had failed.

  - 103 test cases were not executed under a RBT.

- 9 defects were raised

  - 1 defect was deferred (detailed in section 7)

  - 4 defects were accepted

  - 2 defect was closed

  - 2 defects remained open with accepted workarounds (detailed section 7)

# Test Coverage

## Meter Firmware 08.02.R64 – U1300 and U3400

Meter Firmware 08.02.R64 was tested on the combination shown in Table 1. This testing results for the mentioned combination are applicable for both UE and VPN meters as UE and VPN have the same meter type, meter firmware, NIC firmware and UIQ versions.

Meter Types

| Meter Type | Short Description | Meter Firmware | NIC Variant | NIC Firmware |
| --- | --- | --- | --- | --- |
| U3400- 31ML3 | L+G IEC U3400 3PH DIR CONN LC HAN | 08.02.R64 | NIC320/NIC420 | 5.4.33 |
| U3400- 31ML5 | L+G IEC U3400 3PH DIR CONN LC HAN | 08.02.R64 | NIC520 | 5.4.53 |
| U1300-11ML3 | L+G IEC U1300 1PH 1E LC HAN | 08.02.R64 | NIC320/NIC420 | 5.4.33 |
| U1300-11ML5 | L+G IEC U1300 1PH 1E LC HAN | 08.02.R64 | NIC520 | 5.4.53 |

Table 1: Meter Types

UIQ5 Applications

| Application | Description | Version | Build |
| --- | --- | --- | --- |
| CAAS | CAAS | 1.11.6 | 2001300 |
| AMM | Advanced Metering Manager | 5.0.14-REV13 | 2003564 |
| FWU | Firmware Upgrader | 4.16.8 | 2001078 |
| FSU-SAM | FSU Secure Access Manager | 5.2.6b | 2000472 |
| Gridscape | Gridscape | 2.4.3 | 2002372 |
| HCM | HAN Communications Manager | 2.5.5 | 2001465 |
| MPC | Meter Program Configurator | 4.16.7 | 2000715 |
| NC | Network Center | 1.8.5 | 2001201 |
| ODS | Outage Detection System | 5.1.3 | 2000598 |
| SIQ | SensorIQ | 4.0.8 | 2001179 |
| NetMgr | Net Manager | 05.03.99a9.03 |  |
| CATools | CA Tools | 7.5.6 |  |

Table 2 : UIQ5 Application

# Exit Criteria

| Entry / Exit | Criteria |
| --- | --- |
| Exit | - All planned test cases have been executed unless otherwise agreed by the project management team - Supporting evidence (inclusive of input & output data and results) for completed and attempted test cases is captured in HP ALM for review - All defects have been logged in HP ALM - For a Risk Based Test Approach - Execution of all priority 1 test cases and the agreed percentage of priority 2 and 3 test cases is complete - 0 Severity 1 or 2 Defects are outstanding - 2 Severity 3 or 4 Defects have been Accepted, 1 Severity 3 or 4 Defect is closed, 1 Severity 3 or 4 Defects are deferred, and 3 Severity 3 or 4 Defects are open. - All workarounds associated with Defects have been identified and agreed - Test Summary Report has been Approved [this document] |

# Test Execution Summary

The 08.02.R64 meter firmware was tested in the Dev Environment. . The test summary report is attached for reference.

## 08.02.R64 meter firmware

The test result summary is as per the table below.

| Test Set | Failed | N/A | Passed | RBT | Blocked | Not Completed | Grand Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| U1300 R6.4 - NIC3/NIC4 | 7 | 3 | 56 | 24 | 0 | 0 | 90 |
| U1300 R6.4 - NIC5 | 7 | 3 | 52 | 28 | 0 | 0 | 90 |
| U3400 R6.4 - NIC3/NIC4 | 4 | 3 | 56 | 26 | 2 | 0 | 91 |
| U3400 R6.4 - NIC5 | 4 | 3 | 59 | 25 | 0 | 0 | 91 |
| Grand Total | 22 | 12 | 223 | 103 | 2 | 0 | 362 |

Table 3: Test Summary

## Exceptions

Below is a summary of failed test cases. Additional detail is present in the attachment in Appendix 10.1.2  and defects associated to them in Section 7. There are different meter types being tested so it had been the case that particular test case fails on all the meter types which makes the number of failed test cases higher but there is single defect raised for that defect, mentioning all meter types and linked to all the failed test cases.

| Test Area | Failed |
| --- | --- |
| U1300 | 14 |
| Load Contactor – Remote Override Open | 2 |
| Broadcast- Load Contactor | 4 |
| Meter Program - Remote | 6 |
| Load Contactor – Boost Primacy | 2 |
| U3400 | 8 |
| Load Contactor – Remote Override Open | 2 |
| Broadcast- Load Contactor | 4 |
| Load Contactor – Boost Primacy | 2 |
| Grand Total | 22 |

Table 4: Test Failure Summary

# Defect Summary

Defects identified during 08.02.R64 testing are summarised below.

| UIQ v5 Upgrade (VPN & UE) – Phase 2b |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Severity 1 | Severity 2 | Severity 3 | Severity 4 | Total |
|  | Critical | High | Medium | Low |  |
| Accepted |  |  | 3 | 1 | 4 |
| Closed |  | 1 | 1 |  | 2 |
| Deferred |  |  | 1 |  | 1 |
| Rejected |  |  |  |  |  |
| Pending CR |  |  |  |  |  |
| Total Resolved |  |  |  |  |  |
| Open |  |  | 2 |  | 2 |
| Waiting Vendor |  |  |  |  |  |
| Total Project Closure |  |  |  |  |  |
| Total Defects |  | 1 | 7 | 1 | 9 |

Table 5: Defect Summary

## Accepted Defects

There were 3 accepted defects as a result of these testing activities.

| ID | Severity | Defect Summary | Accepted By |
| --- | --- | --- | --- |
| 307 | 3-Medium | Program ID is changed after U3400 Meter FW R.5.54/R8.1.59 are upgraded to R8.02.R64 | Leonard Jarillas |
| 308 | 3-Medium | Program ID is changed after U1300 Meter FW R.5.54 is upgraded to R8.02.R64 | Leonard Jarillas |
| 311 | 3-Medium | Meter FW Upgrade cancels the Priority override command, due to reboot after Meter FW upgrade completion | Leonard Jarillas |
| 313 | 4-Low | Few parameters in MPR file mismatch when meters are upgraded from R54 and R59 to R64 | Leonard Jarillas |

Table 6: Accepted Defects

## Deferred Defects

Deferred defects are considered resolved for the purpose of this release, all deferrals have been agreed with business owners.

There were 1 deferred defects as a result of these testing activities at the time of writing.

| ID | Severity | Defect Summary | Remarks / Workaround |
| --- | --- | --- | --- |
| 304 | 3-Medium | UiQ broadcast job to Connect or Disconnect Load Control Switch 1 with randomization on U1300 meters running 5.4.0053 NIC firmware not working | Itron investigation on solution whether NIC firmware or UIQ update |

Table 7: Deferred Defects

## Fix by Project Closure

Open, with vendor defects.

There are 3 open defects as a result of these testing activities at the time of writing. Some of these defects have workarounds that have been accepted by the business stakeholders but still need a permanent fix by the vendor.

Open Defects

| ID | Severity | Defect Summary | Target Release | Remarks / Workaround |
| --- | --- | --- | --- | --- |
| 309 | 3-Medium | On Demand Auxiliary Switch (LC Swich 1) Open control command, sent from UiQ, does not follow the randomisation periods sent with the command. |  | Workaround: On demand LC close is resolved. On demand LC open works for duration but does not randomise the timing. LC open randomisation can be achieved by executing the partial programming script for LC Open procedure. This partial program script is attached with the defect 309 attachement- “LC Open Randomisation Issue_WithPartialScript.docx” REQ000000277438 |
| 183 | 3-Medium | Itron_AMM_For LnG U1300 and U3400 Meters Enabling boost primacy while the boost primacy is already enabled - disables the boost primacy fully |  | Workaround: This issue can be resolved by reprogramming the meter. REQ000000212201, CS0084935, CS0087282 |

Table 8: Open Defects

# Identified Risks

| Ref | Description | Details | Mitigation |
| --- | --- | --- | --- |
| 1. | Firmware downgrade not supported | Once upgraded to the new 08.02.R64 firmware, the meter will not be able to go back to the non-MS firmware. | Critical tests have been done during testing. Staged deployment of the meter firmware. |
| 2. | Accidental disabling of boost primacy | When a boost primacy enable command is sent to a meter that already has boost primacy enabled, the boost primacy will permanently get disabled. | Program the meter to re-enable boost primacy. |
| 3 | False indication of U1300 – R6.4 - LC override command result | U1300 - R6.4 - UIQ5 indicates LC override command failed with the error - 'Switch failed to close' but the switch closes within the randomization period. The correct status can be checked by refreshing the UIQ page, or by rechecking the status of Auxilliary Switch. | Refresh page or re-query the status |
| 4. | Cacellation of Priority override command due to Meter upgrade | If the meter firmware upgrade is performed while priority override command is being executed for the given duration. Once the meter is upgraded successfully meter reboots and the priority override command is cancelled for the remaining duration. The Auxilliary switch attains the default state as per the schedule. | Avoid the meter firmware upgrade when priority override commands (e.g. broadcast command for hot watel load) are to be executed. |
| 5. | Challenge to bring the meters to active state after the FW upgrade | When the meter FW is upgraded to R64 the program ID of the meter is changed. This bring the meter to initialize state. The program needs to be approved to bring the meter to active state. | The meter FW upgrade activity can be performed on one meter for each program ID. Once the new program ID for each corresponding old program IDs are approved, then the mass meter FW upgrade shall be performed. In this case meters will be able to move to active state once the program mismatch is accepted for those meters in bulk. |

Table 9: Identified Risks

# Location of defects and test results

Detail the location of any and all test results and supporting documentation.  This can include the directory name for any spreadsheet used for recording, or the name of the database name used.  This also includes the name of the Toolset database name.

Project defects and test results are tracked in Application Lifecycle Management (ALM).

## Location of Tests

| URL | http://covmwnedc1hqcp1:8080/qcbin/start_a.jsp |
| --- | --- |
| DOMAIN | TESTING_SERVICES |
| PROJECT | NC_QUALITY |
| RELEASE | 2024 - L&G R8.2 FW |
| PHASE 2B – 08.02.R64 Meter Firmware |  |
| CYCLES | L&G 82-T02, L&G 82-R64 |
| Test Lab | Root\VPN\2024 – LnG 8.2R6.4FW\R64 Root\VPN\2024 – LnG 8.2R6.4FW\T02 |

# Appendix

Include exports from ALM for the execution results and defects.

## Firmware Release Notes

Attached below are the Firmware Release Notes for U1300 and U3400 for Meter FW R64:

## Test results

Attached below are a spreadsheets providing information for the following. The latest results are on ALM.

Overall Test Case Results and Defects.

Attached below are execution results for the testing activities described in this document.

Exceptions

Summary of meter FW 08.02.R64 failed test cases is attached.

## Meter FW 08.02.R64 Defects Workarounds

Attached below are Workarounds to defects found (and remaining without a fix) meter FW 08.02.R64 Upgrade project is proposing to go-live with.

## Deployment Notes

Meter FW 08.02.R64 upgrade is applicable only for U3400 meters

- 08.02.R64 FW build reallocated memory for LP channel; the new location of the LP channel data used the default (unprogrammed) values which pointed to an incorrect location.  When the meter was power cycled the meter suffered a fatal error and was “bricked”. This was the issue for manufacturing.

- To resolve the above issue there was another meter FW release R65, which was identified with another related defect; during the FW upgrade process the Load Control tables were extended.  If the power cycle occurred before the new CRC value could be calculated an error would occur.  To resolve this issue the calculation of the Load Control tables CRC value delayed so it would occur after the power cycle.

- The new Meter Firmware 08.02.R66 which resolves the above two issues will be tested against the DPI requirement coverage.

- As these defects are applicable for U1300 meter, only U3400 meters will be upgraded to R64 meter FW and U1300 meters will be skipped for R64 meter firmware upgrade.

Meter FW upgrade from R54/R59 to 08.02.R64

- The meter program ID will be changed after the meter firmware upgrade. Target one meter each on all program IDs and approve the new meter program IDs after the upgrade.

- Once all the new program IDs are available in AMM for all corresponding old program IDs, mass meter upgrade can be performed.

- After the mass meter upgrade, all the meters can be moved from initialize state to active stae simultaneously, belonging to same program ID.

Configuration for Market Syetm Tool should be updated

- After the Meter Firmware upgrade, AMM program ID is changed on the meters. The configuration for AMM program ID should be upated in the market system tool configuration accordingly.

- New meter programs are developed for meter firmware R64. Once upladed to UIQ, it will have new MPC program ID. So, these MPC program ID should be updated.

Meter FW upgrade during Priority Override in progress

- When meter is rebooted due to successful meter firmware upgrade, and there is priority override already being executed on the meter prior to reboot, the priority override is cancelled for any remaining time after the reboot.

- Auxilliary switch acquires the connect or disconnect state as per the schedule in meter program.

- Avoid upgrading the meter during priority override execution duration.

Boost primacy on upgraded meters

- If Boost Primacy enable is requested consecutively twice, then the boost primacy will be disabled permanently.

- Once the Boost Primacy is disabled, it can be reenabled only by reprogramming the meter.

Meter Program export XML file

- The meter firmware 08.02.R64 upgrade also updates the table 2105, offset 260, length 15 bytes for Modem reset parameters. These parameters are set to default values once the meter upgrade is successfully completed.

- Whereas the meter program XML file that is generated from the latest available version of MCD export tool, has all these 15 bytes set to all 0s. and when the MPC tries to update the meter program using this XML file, these 0s are rejected and default values are set in the meter by meter FW. This causes a mismatch between actual program on the meter and the program file on MPC.

- To resolve this issue, the XML file generated from the MCD export tool shall be modified for table 2105, offset 260, and length 15 bytes to the default modem reset parameters values as per the FW before uploading this XML file to MPC.

- L&G has  provided the updated version of EMPWin+ 6.7.10 tool to resolve this issue. Use the MCD Export from that installation to generate the MCD export file.

# Result and Recommendation

The R64 firmware is tested against the test plan. It is found that it resolves the existing defects related to corrupting U-Series meters data while upgrading the meter for previous meter firmware version.

There are no new severity-1 or severity-2 defects exist on the R64 firmware. All the severity-3 and severity-4 defects have the workaround.

It is recommended to go ahead with the R64 meter firmware upgrade in the production.

# Definitions and Acronyms

| Term | Definition |
| --- | --- |
| AEMO | Australian Energy Market Operator |
| APs | Access Points |
| B2BSO | B2B Service Orders |
| CP | CitiPower |
| ALM | Application Lifecyle Management |
| SIT | System Integration Testing |
| UAT | User Acceptance Testing |
| RBT | Risk Based Testing |

# Revision

| Version | Date | Updated by | Comments |
| --- | --- | --- | --- |
| 0.1 | 28 October 2024 | MK | Initial |
| 1.0 | 12/02/2025 | MK | Final |