NIC Firmware 5.4.53

Test Summary Report

NIC FW 5.4.53 DLMS Meter Upgrade (VPN & UE) Project

Document Control

| Version No: | 1.0 |
| --- | --- |
| Created On: | 19 June 2025 |
| Last Updated: | 23 July 2025 |
| Status: | Final |
| Author/s: | Manoj Kalra |

Approval Status

| Stakeholder Role | Stakeholder Name | Signature | Date |
| --- | --- | --- | --- |
| Network Intelligence Manager | Tobie DeVilliers |  | 24-July-2025 |
| Communications Manager | Stuart Bannister |  |  |
| Meter Asset Manager | Goutham Lingam |  | 23-July-2025 |
| IOT System Service Lead | Wilton Gao |  | 23-July-2025 |
| Market & Meter Data Manager | Jack Friel |  | 24-July-2025 |
| Manager Communication Networks Quality | Leonard Jarillas |  | 24-July-2025 |

Document Purpose

The purpose of the Test Summary Report is to record the results of testing for the NIC Firmware 5.4.53 for Secure DLMS meters.  This document will provide a synopsis of the testing planned, any variations to this plan and details of the results

Included in this document is an overview of Defects, providing Stakeholders with a view of the issues raised during testing and actions for any unresolved defects at the time the testing was completed.  This document will be used as an approval point prior to Deployment.

Related Documents

This section will list related documents. Please note that if this document is updated these related documents may also need to be changed.

| Document | Location | Relationship |
| --- | --- | --- |
| UtilOS® Firmware 5.4.0–5.4.3 Release Notes.pdf | Appendix: 10.1 Firmware Release Notes | Scope |

Reviewers

List the relevant reviewers who are responsible for the deliverables defined in this document.

| Reviewer | Name | Comments/Approval |
| --- | --- | --- |
| UIQ Systems Analyst (VPN) | Nelson Manio |  |
| UIQ Systems Analyst (UE) | Amy Fan | Reviewed |
| Metering Engineer (UE) | Fabian Perez | Reviewed |
| AMI Data Team Lead | Wayne Johnson |  |
| AMI Data Team Lead | Karen Krizmanic |  |
| Market & Meter Data Team Leader | Can Turk | Reviewed |
| AMI Communications Control Operator | Percy Arachchige | Reviewed |
| AMI Communications Analyst | Wayne Sangsukdee |  |
| AMI Communications Analyst | Jogy Cherian |  |
| Communications Network Laboratory Technician | Kamau Njuguna |  |
| Smart Grid Systems Engineer | Abel Lopez |  |
| Metering Engineer | Karl Ngo |  |
| Asset Engineer (Distribution Intelligence) | Hansi Rajapaksha Vithanage Dona |  |
| Senior AMI Strategy Engineer | Graeme Watson | Reviewed |

Contents

1.	Introduction	4

2.	Deviations from Test Plan	4

3.	Summary of Test Activity	4

4.	Test Coverage	4

4.1.	NIC Firmware – DLMS Sprint 210, iCredit 510, and Premier 210	4

5.	Exit Criteria	6

6.	Test Execution Summary	7

6.1.	5.4.53 NIC firmware (VPN & UE)	7

6.2.	Exceptions	7

7.	Defect Summary	8

7.1.	Accepted Defects	8

8.	Identified Risks	8

9.	Location of defects and test results	9

9.1.	Location of Tests	9

10.	Appendix	9

10.1.	Firmware Release Notes	9

10.2.	Test results	9

10.2.1.	Overall Test Case Results and Defects.	9

10.2.2.	Exceptions	9

10.3.	DLMS Meters NIC FW 5.4.53 Defects Workarounds	10

10.4.	Deployment Notes	10

10.4.1.	Auto Disconnection alarms	10

10.4.2.	NIC FW upgrade in Non-Prod Environment	10

11.	Definitions and Acronyms	10

12.	Revision	10

# Introduction

There were existing production NIC firmware defects. The new NIC firmware 5.4.x3 is released from Itron to address those defects. The details of the defects being resolved with this NIC firmware are mentioned in the Release notes attached in the section 10.1. This firmware will be used to baseline and upgrade the production Secure DLMS meters, those are on NIC FW 5.4.50 or earlier.

The purpose of the Test Summary Report is to record the results of testing of the NIC FW 5.4.53 on VPN meters under UIQ v5.  This document will provide a synopsis of the firmware covered and details of the results.

Included in this document is an overview of Defects, providing Stakeholders with a view of the issues raised during testing and actions for any unresolved defects or outstanding test items.  This document will be used as an approval point prior to deploy to production.

# Deviations from Test Plan

As there were no formal Test Plan document created for this testing activity. There were predefined test set that were used to perform the testing for new NIC FW.

Table 1: NIC-Meter Combination

| Meter Type | NIC Type | Status | Remarks |
| --- | --- | --- | --- |
| Secure DPI Sprint 210 | RNI | Tested |  |
| Secure DPI iCredit 510 | RNI | Tested |  |
| Secure DPI Premier 210 | RNI | Tested |  |

# Summary of Test Activity

Testing for NIC Firmware 5.4.53 on Secure DLMS meters was completed on 08/05/2025. Testing was mainly conducted in the UIQ DEV (VPN) environments.

Summarising the testing:

- 87 test cases were initially assigned for execution during these testing activities.

  - During execution 20 test cases were marked as not applicable.

- 59 test cases had passed, and 5 test cases had failed.

- 3 test cases were not executed under an RBT.

- 2 defects were raised

  - 2 defects were accepted (detailed in section 7)

# Test Coverage

## NIC Firmware – DLMS Sprint 210, iCredit 510, and Premier 210

Secure DPI Sprint 210, Secure DPI iCredit 510, and Secure DPI Premier 210 meters on meter firmware FPGCG01, FPH7G01 and FPGDG01 respectively, are tested for NIC 5.4.53.

This was done on VPN meters in UIQ Dev environment. These testing results for the mentioned combination are applicable for both UE and VPN meters as UE and VPN have the same meter type, meter firmware, NIC firmware and UIQ versions.

Meter Types

Table 2: Meter Type

| Meter Type | Short Description | Meter Firmware | NIC Variant | NIC Firmware |
| --- | --- | --- | --- | --- |
| Secure DPI Sprint 210 | Secure DPI Sprint 210 DLMS/COSEM RD 1E 1LC | FPGCG01 | NIC520 | 5.4.53 |
|  | Secure DPI Sprint 210 DLMS/COSEM RD 1E 2LC |  |  |  |
| Secure DPI iCredit 510 | Secure DPI iCredit 510 DLMS/COSEM RD 1E 1LC | FPH7G01 | NIC520 | 5.4.53 |
|  | Secure DPI iCredit 510 DLMS/COSEM RD 1E 2LC |  |  |  |
|  | Secure DPI iCredit 510 DLMS/COSEM RD 2E 2LC |  |  |  |
| Secure DPI Premier 210 | Secure DPI Premier 210 DLMS/COSEM 1E 1LC | FPGDG01 | NIC520 | 5.4.53 |

UIQ5 Applications

Table3: UIQ5 Applications

| Application | Description | Version | Build |
| --- | --- | --- | --- |
| CAAS | CAAS | 1.11.6 | 2001300 |
| AMM | Advanced Metering Manager | 5.0.14-REV13 | 2003564 |
| FWU | Firmware Upgrader | 4.16.8 | 2001078 |
| FSU-SAM | FSU Secure Access Manager | 5.2.6b | 2000472 |
| HCM | HAN Communications Manager | 2.5.5 | 2001465 |
| MPC | Meter Program Configurator | 4.16.7 | 2000715 |
| NC | Network Center | 1.8.5 | 2001201 |
| SIQ | SensorIQ | 4.0.8 | 2001179 |
| NetMgr | Net Manager | 05.03.99a9.03 |  |
| Gridscape | Gridscape | 2.4.3 | 2002372 |

# Exit Criteria

| Entry / Exit | Criteria |
| --- | --- |
| Exit | - All planned test cases have been executed unless otherwise agreed by the project management team. - Supporting evidence (inclusive of input & output data and results) for completed and attempted test cases is captured in HP ALM for review. - All defects have been logged in HP ALM. - For a Risk Based Test Approach - Execution of all priority 1 test cases and the agreed percentage of priority 2 and 3 test cases is complete. - No Severity 1 or 2 Defects are outstanding. - All Severity 3 and 4 Defects have been Accepted. - All workarounds associated with Defects have been identified and agreed. - Test Summary Report has been Approve [this document]. |

# Test Execution Summary

5.4.53 NIC firmware was tested in the Dev environment. The test summary report is attached for reference.

## 5.4.53 NIC firmware (VPN & UE)

The test result summary is as per the table below.

Table 4: Test Result Summary

| Test Set | Failed | N/A | Passed | RBT | Blocked | Not Completed | Grand Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Secure DPI iCredit 510 – NIC 5.4.53 | 2 | 6 | 20 | 1 | 0 | 0 | 29 |
| Secure DPI Sprint 210 – NIC 5.4.53 | 2 | 5 | 21 | 1 | 0 | 0 | 29 |
| Secure DPI Premier 210 – NIC 5.4.53 | 1 | 9 | 18 | 1 | 0 | 0 | 29 |
| Grand Total | 5 | 20 | 59 | 3 | 0 | 0 | 87 |

## Exceptions

Below is a summary of failed test cases. Additional detail is present in the attachment in Appendix 10.1.2 and defects associated to them in Defect Summary.

Table 5: Test Failure Summary

| Test Area | Failed |
| --- | --- |
| Secure DPI iCredit 510 | 2 |
| NIC Firmware- Upgrade | 1 |
| Auto-Disconnect – Enabled: Alarm | 1 |
| Secure DPI Sprint 210 | 2 |
| NIC Firmware- Upgrade | 1 |
| Auto-Disconnect – Enabled: Alarm | 1 |
| Secure DPI Premier 210 | 1 |
| NIC Firmware- Upgrade | 1 |
| Grand Total | 5 |

# Defect Summary

Defects identified during NIC FW 5.4.53 testing are summarised below.

Table 6: Defect Summary

| UIQ v5 Upgrade (VPN & UE) – Phase 2b |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Severity 1 | Severity 2 | Severity 3 | Severity 4 | Total |
|  | Critical | High | Medium | Low |  |
| Accepted |  |  | 1 | 1 | 2 |
| Closed |  |  |  |  |  |
| Deferred |  |  |  |  |  |
| Rejected |  |  |  |  |  |
| Pending CR |  |  |  |  |  |
| Total Resolved |  |  |  |  |  |
| Open |  |  |  |  |  |
| Waiting Vendor |  |  |  |  |  |
| Total Project Closure |  |  |  |  |  |
| Total Defects |  |  | 1 | 1 | 2 |

## Accepted Defects

There is 1 accepted defect as a result of previous testing activities.

Table 7: Existing Accepted Defects

| ID | Severity | Defect Summary | Accepted By |
| --- | --- | --- | --- |
| 290 | 4-Low | SECURE_DLMS_No alarm received on auto-disconnection | Leonard Jarillas |

There is 1 accepted defect as a result of current testing activities. As in the production environment this activity is automatically taken care by the sync performed between different database of AMM and FU applications. This can be environment (non-prod) issue, and need to be checked during BVT.

Table 8: Accepted Defects (New)

| ID | Severity | Defect Summary | Accepted By |
| --- | --- | --- | --- |
| 303 | 3-Medium | NIC Firmware Upgrade not Updated in AMM Device History Page and Device Details Page _VPN UiQ DEV Environment | Leonard Jarillas |

# Identified Risks

There is no identified risk, though, there are some key points that should be taken care when the meters are on 5.4.53 NIC FW. These are mentioned in the deployment notes.

# Location of defects and test results

Detail the location of any and all test results and supporting documentation.  This can include the directory name for any spreadsheet used for recording, or the name of the database name used.  This also includes the name of the Toolset database name.

Project defects and test results are tracked in Application Lifecycle Management (ALM).

## Location of Tests

| URL | http://covmwnedc1hqcp1:8080/qcbin/start_a.jsp |
| --- | --- |
| DOMAIN | TESTING_SERVICES |
| PROJECT | NC_QUALITY |
| RELEASE | 2024 - FW 5.4.3 Meter_NIC |
| 5.4.53 NIC Firmware |  |
| CYCLES | Cycle3 |
| Test Lab | Root\VPN\2024 - FW 5.4.3 Meter_NIC \ 03 PRI-DLMS\24 PRI 1xMP5-NIC5 (C) Root\VPN\2024 - FW 5.4.3 Meter_NIC \ 03 PRI-DLMS\25 PRI 3xMP5-NIC5 (C) Root\VPN\2024 - FW 5.4.3 Meter_NIC \ 03 PRI-DLMS\ 26 PRI CxMP5-NIC5 |

# Appendix

## Firmware Release Notes

Attached below are the NIC Firmware Release Notes for 5.4.53:

Include exports from ALM for the execution results and defects.

## Test results

Attached below are spreadsheets providing information for the following. The latest results are on ALM.

Overall Test Case Results and Defects.

Attached below are execution results for the testing activities described in this document.

Exceptions

Summary of NIC FW 5.4.53 failed test cases is attached.

## DLMS Meters NIC FW 5.4.53 Defects Workarounds

Attached below are Workarounds to defects found (and remaining without a fix) in DLMS meters NIC FW 5.4.53 Upgrade project is proposing to go-live with.

## Deployment Notes

Auto Disconnection alarms

If the meters are Auto Disconnected due to load exceeding the set limit, it may happen that the alarms are missed on UIQ. The meter can be analysed using the events stored in the meter. There will be corresponding Auto Disconnection event stored in the meters.

NIC FW upgrade in Non-Prod Environment

If the NIC FW is upgraded in non-prod environment, it may take little more time when AMM details and device history shows the details of upgraded FW version. So, it is recommended to perform the audit before using the meter for testing on desired NIC FW version in non-prod environment.

# Definitions and Acronyms

| Term | Definition |
| --- | --- |
| AEMO | Australian Energy Market Operator |
| APs | Access Points |
| B2BSO | B2B Service Orders |
| CP | CitiPower |
| ALM | Application Lifecyle Management |
| SIT | System Integration Testing |
| UAT | User Acceptance Testing |
| RBT | Risk Based Testing |

# Revision

| Version | Date | Updated by | Comments |
| --- | --- | --- | --- |
| 1.0 | 04 July 2025 | MK | Final |