## U1300-10ML
1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | U1300 Configuration Developer | [5 empty] | U1300 Configuration Developer | [5 empty] | U1300 Configuration Developer
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Identification | [5 empty] | Identification | [5 empty] | Identification
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Program File ID | 10ML0C1-001 |  |  |  |  | Program File ID | 10ML0A1-003 |  |  |  |  | Program File ID | 10ML0C1-003
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TimeZone | [5 empty] | TimeZone | [5 empty] | TimeZone
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Options | [5 empty] | Options | [5 empty] | Options
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Memory | Extended 1 |  |  |  |  | Memory | Extended 1 |  |  |  |  | Memory | Extended 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Registers | [5 empty] | Registers | [5 empty] | Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | [5 empty] | Number of Rates | [5 empty] | Number of Rates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | 6 |  |  |  |  | Number of Rates | 6 |  |  |  |  | Number of Rates | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Registers | [5 empty] | Energy Registers | [5 empty] | Energy Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register | Description |  |  |  |  | Register | Description |  |  |  |  | Register | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 1 | kWh Imported Element 1 |  |  |  |  | Register 1 | kWh Imported Element 1 |  |  |  |  | Register 1 | kWh Imported Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 2 | kWh Imported Total |  |  |  |  | Register 2 | kWh Imported Total |  |  |  |  | Register 2 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 3 | kWh Exported Element 1 |  |  |  |  | Register 3 | kWh Exported Element 1 |  |  |  |  | Register 3 | kWh Exported Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 4 | kWh Exported Total |  |  |  |  | Register 4 | kWh Exported Total |  |  |  |  | Register 4 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 5 | kVARh Imported Total(Q1+Q2) |  |  |  |  | Register 5 | kVARh Imported Total(Q1+Q2) |  |  |  |  | Register 5 | kVARh Imported Total(Q1+Q2)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 6 | kVARh Exported Total(Q3+Q4) |  |  |  |  | Register 6 | kVARh Exported Total(Q3+Q4) |  |  |  |  | Register 6 | kVARh Exported Total(Q3+Q4)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Description | Value |  |  |  |  | Description | Value |  |  |  |  | Description | Value
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Element 1 | 0 |  |  |  |  | Element 1 | 240 |  |  |  |  | Element 1 | 0
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Element 2 | 0 |  |  |  |  | Element 2 | 240 |  |  |  |  | Element 2 | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Demand | [5 empty] | Demand | [5 empty] | Demand
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero.
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOU Settings | [5 empty] | TOU Settings | [5 empty] | TOU Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Times | [5 empty] | Switch Times | [5 empty] | Switch Times
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Recurring Dates | [5 empty] | Recurring Dates | [5 empty] | Recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-recurring Dates | [5 empty] | Non-recurring Dates | [5 empty] | Non-recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Configuration | [5 empty] | Load Profile Configuration | [5 empty] | Load Profile Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | kWh Imported Total |  |  |  |  | Channel 1 | kWh Imported Total |  |  |  |  | Channel 1 | kWh Imported Total
FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Channel 2 | kWh Exported Total | [10 empty] | Channel 2 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Storage Days | 401 |  |  |  |  | Storage Days | 796 |  |  |  |  | Storage Days | 401
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | Voltage | 60 | 207 | 259 | 100 | Channel 1 | Voltage | 60 | 207 | 259 | 100 | Channel 1 | Voltage | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 2 | Voltage | 60 | 216 | 253 | 100 | Channel 2 | Voltage | 60 | 216 | 253 | 100 | Channel 2 | Voltage | 60 | 216 | 253 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 3 | Current E1 | 60 | -40 | 100 | 100 | Channel 3 | Current E1 | 60 | -40 | 100 | 100 | Channel 3 | Current E1 | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Settings | [5 empty] | Display Settings | [5 empty] | Display Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | No. of Energy Digits | 6 |  |  |  |  | No. of Energy Digits | 6 |  |  |  |  | No. of Energy Digits | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Groups | [5 empty] | Display Groups | [5 empty] | Display Groups
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Display List | [5 empty] | Normal Display List | [5 empty] | Normal Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Date |  |  |  |  | 2 | Date |  |  |  |  | 2 | Date
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | kWh Imported Total |  |  |  |  | 3 | kWh Imported Total |  |  |  |  | 3 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7 | kWh Imported Element 2 |  |  |  |  | 7 | kWh Imported Element 2 |  |  |  |  | 7 | kWh Imported Element 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 88 | Display Test |  |  |  |  | 88 | Display Test |  |  |  |  | 88 | Display Test
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 1 Display List | [5 empty] | Alternative 1 Display List | [5 empty] | Alternative 1 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 23 | Program File ID |  |  |  |  | 23 | Program File ID |  |  |  |  | 23 | Program File ID
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 24 | Program File Version |  |  |  |  | 24 | Program File Version |  |  |  |  | 24 | Program File Version
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 2 Display List | [5 empty] | Alternative 2 Display List | [5 empty] | Alternative 2 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Voltage |  |  |  |  | 1 | Voltage |  |  |  |  | 1 | Voltage
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Amps Element 1 |  |  |  |  | 2 | Amps Element 1 |  |  |  |  | 2 | Amps Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 4 | Power Factor Total |  |  |  |  | 4 | Power Factor Total |  |  |  |  | 4 | Power Factor Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | Frequency |  |  |  |  | 5 | Frequency |  |  |  |  | 5 | Frequency
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 6 | Power Active Total |  |  |  |  | 6 | Power Active Total |  |  |  |  | 6 | Power Active Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7 | Power Reactive Total |  |  |  |  | 7 | Power Reactive Total |  |  |  |  | 7 | Power Reactive Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Settings | [5 empty] | Relay Settings | [5 empty] | Relay Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker | TRUE |  |  |  |  | Breaker | TRUE |  |  |  |  | Breaker | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 | FALSE |  |  |  |  | Controlled Load L1 | FALSE |  |  |  |  | Controlled Load L1 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Arm Setting | [5 empty] | Arm Setting | [5 empty] | Arm Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Group ID Setting | [5 empty] | Group ID Setting | [5 empty] | Group ID Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect | [5 empty] | Auto Disconnect | [5 empty] | Auto Disconnect
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load - General | [5 empty] | Controlled Load - General | [5 empty] | Controlled Load - General
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | [5 empty] | Prepayment | [5 empty] | Prepayment
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Back End Communication | [5 empty] | Back End Communication | [5 empty] | Back End Communication
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem | Not configured |  |  |  |  | Modem | Not configured |  |  |  |  | Modem | Not configured
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Settings | [5 empty] | Event Settings | [5 empty] | Event Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event | Setting |  |  |  |  | Event | Setting |  |  |  |  | Event | Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 1 export energy detected start | Log Only |  |  |  |  | Element 1 export energy detected start | Log Only |  |  |  |  | Element 1 export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 1 export energy detected end | Log Only |  |  |  |  | Element 1 export energy detected end | Log Only |  |  |  |  | Element 1 export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 2 export energy detected start | Log Only |  |  |  |  | Element 2 export energy detected start | Log Only |  |  |  |  | Element 2 export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 2 export energy detected end | Log Only |  |  |  |  | Element 2 export energy detected end | Log Only |  |  |  |  | Element 2 export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Ripple | Log Only |  |  |  |  | Ripple | Log Only |  |  |  |  | Ripple | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Breaker State Change | Log Only |  |  |  |  | Extended Breaker State Change | Log Only |  |  |  |  | Extended Breaker State Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only

## U1300-11ML (hidden)
1 | 2 | 3 | 4 | 5 | 6
U1300 Configuration Developer
Identification
Program File ID | 11MLCC1-001
TimeZone
Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney
Options
Reset Password Lockout On Power Fail | TRUE
Enable Optical Priority | TRUE
Use Crystal for Time Keeping | TRUE
Metering Type | Net Metering
Tamper Event Grace Period (minutes) | 0
Memory | Extended 1
Registers
Number of Rates
Number of Rates | 6
Energy Registers
Register | Description
Register 1 | kWh Imported Element 1
Register 2 | kWh Imported Total
Register 3 | kWh Exported Element 1
Register 4 | kWh Exported Total
Register 5 | kVARh Imported Total(Q1+Q2)
Register 6 | kVARh Exported Total(Q3+Q4)
Export Wh Warning Levels
Description | Value
Element 1 | 0
Element 2 | 0
Demand
Number of demand registers is zero.
TOU Settings
Switch Times
Season No. | Day Type | Time | Rate
Recurring Dates
Month | Day | Offset | Day Of Week | Action | Prev Period Read
Non-recurring Dates
Date | Action | Prev Period Read
Load Profile Configuration
Number Of Groups | 1
LP Group 1 | Load Profile Channel Description
Channel 1 | kWh Imported Total
Channel 2 | kWh Exported Total
Interval minutes | 5 Min
Storage Days | 401
Quality of Supply Configuration
QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events
Channel 1 | Voltage | 60 | 207 | 259 | 100
Channel 2 | Voltage | 60 | 216 | 253 | 100
Channel 3 | Current E1 | 60 | -40 | 100 | 100
Display Settings
Energy Decimal Places | 1
Suppress Leading Zeroes | TRUE
No. of Energy Digits | 6
Display Groups
Normal Display List
Scroll Time [Secs] 5
Display ID | Description
1 | Time(hh:mm ss)
2 | Date
3 | kWh Imported Total
5 | kWh Exported Total
7 | kWh Imported Element 2
88 | Display Test
Alternative 1 Display List
Scroll Time [Secs] 5
Display ID | Description
20 | Serial No First 7
21 | Serial No Mid 7
22 | Firmware Revision
23 | Program File ID
24 | Program File Version
25 | Hardware Revision
26 | Standard Meter Status
27 | Manufacturer Meter Status
28 | Estimated % Battery Life Remaining
Alternative 2 Display List
Scroll Time [Secs] 5
Display ID | Description
1 | Voltage
2 | Amps Element 1
4 | Power Factor Total
5 | Frequency
6 | Power Active Total
7 | Power Reactive Total
Relay Settings
Relay Present Mask Setting
Breaker | TRUE
Controlled Load L1 | TRUE
Controlled Load L2 | FALSE
Arm Setting
Connect Arm | FALSE
Disconnect Arm | FALSE
Randomisation Method | On Power Up
Breaker Arming Timeout
Timeout | 1 Hours
Group ID Setting
Primary Group ID | 20
Secondary Group ID | 200
Tertiary Group ID | 200
Normal Supply Capacity Control
Normal Import Demand Duration [trading intervals] | 1
Normal Import Demand Limit [kW] | 0
Normal Export Demand Duration [trading intervals] | 1
Normal Export Demand Limit [kW] | 0
Normal Supply Reclose Delay [minutes] | 30
Emergency Supply Capacity Control
Emergency Demand Duration [minutes] | 5
Emergency Demand Limit [kW] | 0
Emergency Supply Reclose Delay [minutes] | 15
TOD Import Supply Capacity Control
Monitoring Start Time [HH:MM] | 0:00
Monitoring Duration [minutes] | 5
Import Demand Duration [trading intervals] | 1
Import Demand Limit [kW] | 0
Reclose Delay [minutes] | 1
TOD Export Supply Capacity Control
Monitoring Start Time [HH:MM] | 0:00
Monitoring Duration [minutes] | 5
Export Demand Duration [trading intervals] | 1
Export Demand Limit [kW] | 0
Reclose Delay [minutes] | 1
Supply Capacity Control Initial Settings
Enable Normal SCC | FALSE
Enable Emergency SCC | FALSE
Enable TodImport SCC | FALSE
Enable TodExport SCC | FALSE
Auto Disconnect
Auto Disconnect Monitoring Period [seconds] | 5
Auto Disconnect Demand Limit [W] | 20
Auto Disconnect Breach Time [seconds] | 3
Breaker Loss of Supply
Enable Loss of Supply | FALSE
Controlled Load - General
| Ignore time table delay on power up | FALSE
U1200 Compatibility Mode | FALSE
Controlled Load L1 Functionalities
Loss of Supply
Support Loss of Supply | FALSE
Power Restore
Support Power Restore | FALSE
Priority Override
Support Priority Override | TRUE
Override Period (HH:MM) | 8:00
| Minimum | Maximum
Random Delay (HH:MM) | 0:00 | 0:00
Boost
Support Boost | TRUE
Boost Duration | 8 hours
Allow to stop boost by pressing boost button | TRUE
Boost To Element 1 | TRUE
Stop boost when ESCC is enabled | TRUE
Boost Primacy Initial Command
Enable Boost Primacy | TRUE
Under Frequency Load Control (UFLC)
Support Under Frequency Load Control | FALSE
Demand Limiting Load Control (DLLC)
Support Demand Limiting Load Control | FALSE
Time Table
Support Time Table | TRUE
General Settings
| Minimum | Maximum
Random Delay (HH:MM) | 0:00 | 0:30
Default Relay Action | Open
Cycler Configuration
Cycler Type | Standard
| Minimum | Maximum
Initial Delay(T1) | 0:00 | 0:00
Close Duration(T2) | 0:01
Open Duration(T3) | 0:01
Season Switch Dates
Month | Day | Offset | Day Of Week | Action
January | 1 | No Offset |  | Season Change 0
Season 0 Normal Scheduler
Switch Table A
Switch Time | Action
7:00 | Instant Open
23:00 | Delayed Close
Applies to
Monday
Tuesday
Wednesday
Thursday
Friday
Saturday
Sunday
Switch Table B
Switch Time | Action
Applies to
Ripple
Support Ripple Control | FALSE
Prepayment
Support Prepayment | FALSE
Back End Communication
Modem | Not configured
Modem Reset Type | None
Event Settings
Event | Setting
Primary Power Down | Log Only
Primary Power Up | Log Only
Time Changed (old time used as time stamp) | Log Only
Time Changed (new time used as time stamp) | Log Only
Procedure Invoked | Log Only
Table Written To | Log Only
Reset List Pointers | Log Only
Event Log Cleared | Log Only
Season Changed | Log Only
Special Schedule Activated | Log Only
Self check error detected | Log Only
Non-volatile memory failure detected | Log Only
Measurement error detected | Log Only
Low battery detected | Log Only
Tamper attempt detected | Log Only
QOS threshold I breach start | Log Only
QOS threshold I breach end | Log Only
QOS threshold II breach start | Log Only
QOS threshold II breach end | Log Only
QOS threshold III breach start | Log Only
QOS threshold III breach end | Log Only
Element 1 export energy detected start | Log Only
Element 1 export energy detected end | Log Only
Element 2 export energy detected start | Log Only
Element 2 export energy detected end | Log Only
Service Disconnect open | Log Only
Service Disconnect close | Log Only
Service Disconnect armed for open | Log Only
Service Disconnect armed for close | Log Only
Controlled Load L1 open | Log Only
Controlled Load L1 close | Log Only
Controlled Load L2 open | Log Only
Controlled Load L2 close | Log Only
Primary group command accepted | Log Only
Primary group command rejected | Log Only
Secondary group command accepted | Log Only
Secondary group command rejected | Log Only
Tertiary group command accepted | Log Only
Tertiary group command rejected | Log Only
Service Disconnect open due to auto-disconnect | Alarm
Service Disconnect open due to supply capacity | Alarm
Service Disconnect close after supply capacity timeout. | Alarm
Controlled Load override. | Log Only
Multiple events logged today | Log Only
Controlled Load override timer expired. | Log Only
Controlled Load closed due to boost. | Log Only
Reprogramming | Log Only
Scroll button pressed | Log Only
Alt button pressed | Log Only
Boost button pressed | Log Only
Service Disconnect close acknowledged | Log Only
Service Disconnect open acknowledged | Log Only
Primary group command table write | Log Only
Secondary group command table write | Log Only
Tertiary group command table write | Log Only
Failed password on login | Log Only
Multiple failed logins | Log Only
Communication lockout | Log Only
Firmware changed | Log Only
Master group command accepted | Log Only
Master group command rejected | Log Only
Local Parameter Change | Log Only
Remote Power Fail | Log Only
Communications Update | Log Only
Load Profile Status Change | Log Only
Multi Source Tamper | Log Only
Extended Load Control | Log Only
Ripple | Log Only
Critical Table Changed | Log Only
Prepayment | Log Only
Breaker LOS | Log Only
Extended Breaker State Change | Log Only
Extended Event | Log Only

## U1300-12ML
1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | U1300 Configuration Developer | [5 empty] | U1300 Configuration Developer | [5 empty] | U1300 Configuration Developer
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Identification | [5 empty] | Identification | [5 empty] | Identification
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Program File ID | 12MLAD2-001 |  |  |  |  | Program File ID | 12MLAD2-003 |  |  |  |  | Program File ID | 12MLAB2-003
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TimeZone | [5 empty] | TimeZone | [5 empty] | TimeZone
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Options | [5 empty] | Options | [5 empty] | Options
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Memory | Extended 1 |  |  |  |  | Memory | Extended 1 |  |  |  |  | Memory | Extended 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Registers | [5 empty] | Registers | [5 empty] | Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | [5 empty] | Number of Rates | [5 empty] | Number of Rates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | 6 |  |  |  |  | Number of Rates | 6 |  |  |  |  | Number of Rates | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Registers | [5 empty] | Energy Registers | [5 empty] | Energy Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register | Description |  |  |  |  | Register | Description |  |  |  |  | Register | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 1 | kWh Imported Element 1 |  |  |  |  | Register 1 | kWh Imported Element 1 |  |  |  |  | Register 1 | kWh Imported Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 2 | kWh Imported Total |  |  |  |  | Register 2 | kWh Imported Total |  |  |  |  | Register 2 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 3 | kWh Exported Element 1 |  |  |  |  | Register 3 | kWh Exported Element 1 |  |  |  |  | Register 3 | kWh Exported Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 4 | kWh Exported Total |  |  |  |  | Register 4 | kWh Exported Total |  |  |  |  | Register 4 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 5 | kWh Imported Element 2 |  |  |  |  | Register 5 | kWh Imported Element 2 |  |  |  |  | Register 5 | kWh Imported Element 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 6 | kWh Exported Element 2 |  |  |  |  | Register 6 | kWh Exported Element 2 |  |  |  |  | Register 6 | kWh Exported Element 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Description | Value |  |  |  |  | Description | Value |  |  |  |  | Description | Value
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Element 1 | 0 |  |  |  |  | Element 1 | 0 |  |  |  |  | Element 1 | 240
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Element 2 | 0 |  |  |  |  | Element 2 | 0 |  |  |  |  | Element 2 | 240
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Demand | [5 empty] | Demand | [5 empty] | Demand
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero.
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOU Settings | [5 empty] | TOU Settings | [5 empty] | TOU Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Times | [5 empty] | Switch Times | [5 empty] | Switch Times
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Recurring Dates | [5 empty] | Recurring Dates | [5 empty] | Recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-recurring Dates | [5 empty] | Non-recurring Dates | [5 empty] | Non-recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Configuration | [5 empty] | Load Profile Configuration | [5 empty] | Load Profile Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | kWh Imported Element 1 |  |  |  |  | Channel 1 | kWh Imported Element 1 |  |  |  |  | Channel 1 | kWh Imported Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 2 | kWh Imported Element 2 |  |  |  |  | Channel 2 | kWh Imported Element 2 |  |  |  |  | Channel 2 | kWh Imported Element 2
FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Channel 3 | kWh Exported Total |  |  |  |  | Channel 3 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Storage Days | 302 |  |  |  |  | Storage Days | 302 |  |  |  |  | Storage Days | 401
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | Voltage | 60 | 207 | 259 | 100 | Channel 1 | Voltage | 60 | 207 | 259 | 100 | Channel 1 | Voltage | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 2 | Voltage | 60 | 216 | 253 | 100 | Channel 2 | Voltage | 60 | 216 | 253 | 100 | Channel 2 | Voltage | 60 | 216 | 253 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 3 | Current E1 | 60 | -40 | 100 | 100 | Channel 3 | Current E1 | 60 | -40 | 100 | 100 | Channel 3 | Current E1 | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Settings | [5 empty] | Display Settings | [5 empty] | Display Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | No. of Energy Digits | 6 |  |  |  |  | No. of Energy Digits | 6 |  |  |  |  | No. of Energy Digits | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Groups | [5 empty] | Display Groups | [5 empty] | Display Groups
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Display List | [5 empty] | Normal Display List | [5 empty] | Normal Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Date |  |  |  |  | 2 | Date |  |  |  |  | 2 | Date
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | kWh Imported Element 1 |  |  |  |  | 3 | kWh Imported Element 1 |  |  |  |  | 3 | kWh Imported Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7 | kWh Imported Element 2 |  |  |  |  | 7 | kWh Imported Element 2 |  |  |  |  | 7 | kWh Imported Element 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 88 | Display Test |  |  |  |  | 88 | Display Test |  |  |  |  | 88 | Display Test
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 1 Display List | [5 empty] | Alternative 1 Display List | [5 empty] | Alternative 1 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 23 | Program File ID |  |  |  |  | 23 | Program File ID |  |  |  |  | 23 | Program File ID
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 24 | Program File Version |  |  |  |  | 24 | Program File Version |  |  |  |  | 24 | Program File Version
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 2 Display List | [5 empty] | Alternative 2 Display List | [5 empty] | Alternative 2 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Voltage |  |  |  |  | 1 | Voltage |  |  |  |  | 1 | Voltage
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Amps Element 1 |  |  |  |  | 2 | Amps Element 1 |  |  |  |  | 2 | Amps Element 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | Amps Element 2 |  |  |  |  | 3 | Amps Element 2 |  |  |  |  | 3 | Amps Element 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 4 | Power Factor Total |  |  |  |  | 4 | Power Factor Total |  |  |  |  | 4 | Power Factor Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | Frequency |  |  |  |  | 5 | Frequency |  |  |  |  | 5 | Frequency
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 6 | Power Active Total |  |  |  |  | 6 | Power Active Total |  |  |  |  | 6 | Power Active Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7 | Power Reactive Total |  |  |  |  | 7 | Power Reactive Total |  |  |  |  | 7 | Power Reactive Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Settings | [5 empty] | Relay Settings | [5 empty] | Relay Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker | TRUE |  |  |  |  | Breaker | TRUE |  |  |  |  | Breaker | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 | TRUE |  |  |  |  | Controlled Load L1 | TRUE |  |  |  |  | Controlled Load L1 | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Arm Setting | [5 empty] | Arm Setting | [5 empty] | Arm Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Group ID Setting | [5 empty] | Group ID Setting | [5 empty] | Group ID Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect | [5 empty] | Auto Disconnect | [5 empty] | Auto Disconnect
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load - General | [5 empty] | Controlled Load - General | [5 empty] | Controlled Load - General
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | U1200 Compatibility Mode | FALSE |  |  |  |  | U1200 Compatibility Mode | FALSE |  |  |  |  | U1200 Compatibility Mode | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 Functionalities | [5 empty] | Controlled Load L1 Functionalities | [5 empty] | Controlled Load L1 Functionalities
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Loss of Supply | [5 empty] | Loss of Supply | [5 empty] | Loss of Supply
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Loss of Supply | FALSE |  |  |  |  | Support Loss of Supply | FALSE |  |  |  |  | Support Loss of Supply | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Power Restore | [5 empty] | Power Restore | [5 empty] | Power Restore
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Power Restore | FALSE |  |  |  |  | Support Power Restore | FALSE |  |  |  |  | Support Power Restore | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Priority Override | [5 empty] | Priority Override | [5 empty] | Priority Override
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Priority Override | TRUE |  |  |  |  | Support Priority Override | TRUE |  |  |  |  | Support Priority Override | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Override Period (HH:MM) | 8:00 |  |  |  |  | Override Period (HH:MM) | 8:00 |  |  |  |  | Override Period (HH:MM) | 8:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Random Delay (HH:MM) | 0:00 | 0:00 |  |  |  | Random Delay (HH:MM) | 0:00 | 0:00 |  |  |  | Random Delay (HH:MM) | 0:00 | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost | [5 empty] | Boost | [5 empty] | Boost
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Boost | TRUE |  |  |  |  | Support Boost | TRUE |  |  |  |  | Support Boost | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost Duration | 8 hours |  |  |  |  | Boost Duration | 8 hours |  |  |  |  | Boost Duration | 8 hours
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Allow to stop boost by pressing boost button | TRUE |  |  |  |  | Allow to stop boost by pressing boost button | TRUE |  |  |  |  | Allow to stop boost by pressing boost button | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost To Element 1 | TRUE |  |  |  |  | Boost To Element 1 | TRUE |  |  |  |  | Boost To Element 1 | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Stop boost when ESCC is enabled | TRUE |  |  |  |  | Stop boost when ESCC is enabled | TRUE |  |  |  |  | Stop boost when ESCC is enabled | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost Primacy Initial Command | [5 empty] | Boost Primacy Initial Command | [5 empty] | Boost Primacy Initial Command
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Boost Primacy | TRUE |  |  |  |  | Enable Boost Primacy | TRUE |  |  |  |  | Enable Boost Primacy | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Under Frequency Load Control (UFLC) | [5 empty] | Under Frequency Load Control (UFLC) | [5 empty] | Under Frequency Load Control (UFLC)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Under Frequency Load Control | FALSE |  |  |  |  | Support Under Frequency Load Control | FALSE |  |  |  |  | Support Under Frequency Load Control | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Demand Limiting Load Control (DLLC) | [5 empty] | Demand Limiting Load Control (DLLC) | [5 empty] | Demand Limiting Load Control (DLLC)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Demand Limiting Load Control | FALSE |  |  |  |  | Support Demand Limiting Load Control | FALSE |  |  |  |  | Support Demand Limiting Load Control | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Table | [5 empty] | Time Table | [5 empty] | Time Table
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Time Table | TRUE |  |  |  |  | Support Time Table | TRUE |  |  |  |  | Support Time Table | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | General Settings | [5 empty] | General Settings | [5 empty] | General Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Random Delay (HH:MM) | 0:00 | 1:30 |  |  |  | Random Delay (HH:MM) | 0:00 | 1:30 |  |  |  | Random Delay (HH:MM) | 0:00 | 1:30
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Default Relay Action | Open |  |  |  |  | Default Relay Action | Open |  |  |  |  | Default Relay Action | Open
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cycler Configuration | [5 empty] | Cycler Configuration | [5 empty] | Cycler Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cycler Type | Standard |  |  |  |  | Cycler Type | Standard |  |  |  |  | Cycler Type | Standard
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Initial Delay(T1) | 0:00 | 0:00 |  |  |  | Initial Delay(T1) | 0:00 | 0:00 |  |  |  | Initial Delay(T1) | 0:00 | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Close Duration(T2) | 0:01 |  |  |  |  | Close Duration(T2) | 0:01 |  |  |  |  | Close Duration(T2) | 0:01
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Open Duration(T3) | 0:01 |  |  |  |  | Open Duration(T3) | 0:01 |  |  |  |  | Open Duration(T3) | 0:01
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season Switch Dates | [5 empty] | Season Switch Dates | [5 empty] | Season Switch Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Month | Day | Offset | Day Of Week | Action |  | Month | Day | Offset | Day Of Week | Action |  | Month | Day | Offset | Day Of Week | Action
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | January | 1 | No Offset |  | Season Change 0 |  | January | 1 | No Offset |  | Season Change 0 |  | January | 1 | No Offset |  | Season Change 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season 0 Normal Scheduler | [5 empty] | Season 0 Normal Scheduler | [5 empty] | Season 0 Normal Scheduler
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Table A | [5 empty] | Switch Table A | [5 empty] | Switch Table A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Time | Action |  |  |  |  | Switch Time | Action |  |  |  |  | Switch Time | Action
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7:00 | Instant Open |  |  |  |  | 7:00 | Instant Open |  |  |  |  | 7:00 | Instant Open
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 22:00 | Delayed Close |  |  |  |  | 22:00 | Delayed Close |  |  |  |  | 22:00 | Delayed Close
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Applies to | [5 empty] | Applies to | [5 empty] | Applies to
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monday | [5 empty] | Monday | [5 empty] | Monday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tuesday | [5 empty] | Tuesday | [5 empty] | Tuesday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Wednesday | [5 empty] | Wednesday | [5 empty] | Wednesday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thursday | [5 empty] | Thursday | [5 empty] | Thursday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Friday | [5 empty] | Friday | [5 empty] | Friday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Saturday | [5 empty] | Saturday | [5 empty] | Saturday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Sunday | [5 empty] | Sunday | [5 empty] | Sunday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Table B | [5 empty] | Switch Table B | [5 empty] | Switch Table B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Time | Action |  |  |  |  | Switch Time | Action |  |  |  |  | Switch Time | Action
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Applies to | [5 empty] | Applies to | [5 empty] | Applies to
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Ripple | [5 empty] | Ripple | [5 empty] | Ripple
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Ripple Control | FALSE |  |  |  |  | Support Ripple Control | FALSE |  |  |  |  | Support Ripple Control | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | [5 empty] | Prepayment | [5 empty] | Prepayment
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Back End Communication | [5 empty] | Back End Communication | [5 empty] | Back End Communication
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem | Not configured |  |  |  |  | Modem | Not configured |  |  |  |  | Modem | Not configured
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Settings | [5 empty] | Event Settings | [5 empty] | Event Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event | Setting |  |  |  |  | Event | Setting |  |  |  |  | Event | Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 1 export energy detected start | Log Only |  |  |  |  | Element 1 export energy detected start | Log Only |  |  |  |  | Element 1 export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 1 export energy detected end | Log Only |  |  |  |  | Element 1 export energy detected end | Log Only |  |  |  |  | Element 1 export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 2 export energy detected start | Log Only |  |  |  |  | Element 2 export energy detected start | Log Only |  |  |  |  | Element 2 export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Element 2 export energy detected end | Log Only |  |  |  |  | Element 2 export energy detected end | Log Only |  |  |  |  | Element 2 export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Ripple | Log Only |  |  |  |  | Ripple | Log Only |  |  |  |  | Ripple | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Breaker State Change | Log Only |  |  |  |  | Extended Breaker State Change | Log Only |  |  |  |  | Extended Breaker State Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only

## U3400-30ML3
1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | U3400 Configuration Developer | [5 empty] | U3400 Configuration Developer | [5 empty] | U3400 Configuration Developer
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Identification | [5 empty] | Identification | [5 empty] | Identification
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Program File ID | 30ML0C1-001 |  |  |  |  | Program File ID | 30ML0C1-003 |  |  |  |  | Program File ID | 30ML0A1-003
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TimeZone | [5 empty] | TimeZone | [5 empty] | TimeZone
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Options | [5 empty] | Options | [5 empty] | Options
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Total Metering | Total Phase A+B+C |  |  |  |  | Total Metering | Total Phase A+B+C |  |  |  |  | Total Metering | Total Phase A+B+C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Memory | Extended 1 |  |  |  |  | Memory | Extended 1 |  |  |  |  | Memory | Extended 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Registers | [5 empty] | Registers | [5 empty] | Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | [5 empty] | Number of Rates | [5 empty] | Number of Rates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | 1 |  |  |  |  | Number of Rates | 1 |  |  |  |  | Number of Rates | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Registers | [5 empty] | Energy Registers | [5 empty] | Energy Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register | Description |  |  |  |  | Register | Description |  |  |  |  | Register | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 1 | kWh Imported Total |  |  |  |  | Register 1 | kWh Imported Total |  |  |  |  | Register 1 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 2 | kWh Exported Total |  |  |  |  | Register 2 | kWh Exported Total |  |  |  |  | Register 2 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 3 | kVARh Imported Total(Q1+Q2) |  |  |  |  | Register 3 | kVARh Imported Total(Q1+Q2) |  |  |  |  | Register 3 | kVARh Imported Total(Q1+Q2)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 4 | kVARh Exported Total(Q3+Q4) |  |  |  |  | Register 4 | kVARh Exported Total(Q3+Q4) |  |  |  |  | Register 4 | kVARh Exported Total(Q3+Q4)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 5 | kWh Imported Phase A |  |  |  |  | Register 5 | kWh Imported Phase A |  |  |  |  | Register 5 | kWh Imported Phase A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 6 | kWh Imported Phase B |  |  |  |  | Register 6 | kWh Imported Phase B |  |  |  |  | Register 6 | kWh Imported Phase B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Description | Value |  |  |  |  | Description | Value |  |  |  |  | Description | Value
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Phase A | 0 |  |  |  |  | Phase A | 0 |  |  |  |  | Phase A | 240
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Phase B | 0 |  |  |  |  | Phase B | 0 |  |  |  |  | Phase B | 240
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Phase C | 0 |  |  |  |  | Phase C | 0 |  |  |  |  | Phase C | 240
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Demand | [5 empty] | Demand | [5 empty] | Demand
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero.
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOU Settings | [5 empty] | TOU Settings | [5 empty] | TOU Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Times | [5 empty] | Switch Times | [5 empty] | Switch Times
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Recurring Dates | [5 empty] | Recurring Dates | [5 empty] | Recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-recurring Dates | [5 empty] | Non-recurring Dates | [5 empty] | Non-recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Configuration | [5 empty] | Load Profile Configuration | [5 empty] | Load Profile Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | kWh Imported Total |  |  |  |  | Channel 1 | kWh Imported Total |  |  |  |  | Channel 1 | kWh Imported Total
FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Channel 2 | kWh Exported Total |  |  |  |  | Channel 2 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Storage Days | 401 |  |  |  |  | Storage Days | 401 |  |  |  |  | Storage Days | 796
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | Voltage Phase A | 60 | 207 | 259 | 100 | Channel 1 | Voltage Phase A | 60 | 207 | 259 | 100 | Channel 1 | Voltage Phase A | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 2 | Voltage Phase B | 60 | 207 | 259 | 100 | Channel 2 | Voltage Phase B | 60 | 207 | 259 | 100 | Channel 2 | Voltage Phase B | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 3 | Voltage Phase C | 60 | 207 | 259 | 100 | Channel 3 | Voltage Phase C | 60 | 207 | 259 | 100 | Channel 3 | Voltage Phase C | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 4 | Current Phase A | 60 | -40 | 100 | 100 | Channel 4 | Current Phase A | 60 | -40 | 100 | 100 | Channel 4 | Current Phase A | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 5 | Current Phase B | 60 | -40 | 100 | 100 | Channel 5 | Current Phase B | 60 | -40 | 100 | 100 | Channel 5 | Current Phase B | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 6 | Current Phase C | 60 | -40 | 100 | 100 | Channel 6 | Current Phase C | 60 | -40 | 100 | 100 | Channel 6 | Current Phase C | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Settings | [5 empty] | Display Settings | [5 empty] | Display Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | No. of Energy Digits | 7 |  |  |  |  | No. of Energy Digits | 7 |  |  |  |  | No. of Energy Digits | 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Groups | [5 empty] | Display Groups | [5 empty] | Display Groups
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Display List | [5 empty] | Normal Display List | [5 empty] | Normal Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Date |  |  |  |  | 2 | Date |  |  |  |  | 2 | Date
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | kWh Imported Total |  |  |  |  | 3 | kWh Imported Total |  |  |  |  | 3 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 88 | Display Test |  |  |  |  | 88 | Display Test |  |  |  |  | 88 | Display Test
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 1 Display List | [5 empty] | Alternative 1 Display List | [5 empty] | Alternative 1 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 23 | Program File ID |  |  |  |  | 23 | Program File ID |  |  |  |  | 23 | Program File ID
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 24 | Program File Version |  |  |  |  | 24 | Program File Version |  |  |  |  | 24 | Program File Version
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 2 Display List | [5 empty] | Alternative 2 Display List | [5 empty] | Alternative 2 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Voltage Phase A |  |  |  |  | 1 | Voltage Phase A |  |  |  |  | 1 | Voltage Phase A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Amps Phase A |  |  |  |  | 2 | Amps Phase A |  |  |  |  | 2 | Amps Phase A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | Voltage Phase B |  |  |  |  | 3 | Voltage Phase B |  |  |  |  | 3 | Voltage Phase B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 4 | Amps Phase B |  |  |  |  | 4 | Amps Phase B |  |  |  |  | 4 | Amps Phase B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | Voltage Phase C |  |  |  |  | 5 | Voltage Phase C |  |  |  |  | 5 | Voltage Phase C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 6 | Amps Phase C |  |  |  |  | 6 | Amps Phase C |  |  |  |  | 6 | Amps Phase C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7 | Power Factor Total |  |  |  |  | 7 | Power Factor Total |  |  |  |  | 7 | Power Factor Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 8 | Frequency |  |  |  |  | 8 | Frequency |  |  |  |  | 8 | Frequency
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 9 | Power Active Total |  |  |  |  | 9 | Power Active Total |  |  |  |  | 9 | Power Active Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 10 | Power Reactive Total |  |  |  |  | 10 | Power Reactive Total |  |  |  |  | 10 | Power Reactive Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Settings | [5 empty] | Relay Settings | [5 empty] | Relay Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker | TRUE |  |  |  |  | Breaker | TRUE |  |  |  |  | Breaker | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 | FALSE |  |  |  |  | Controlled Load L1 | FALSE |  |  |  |  | Controlled Load L1 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L3 | FALSE |  |  |  |  | Controlled Load L3 | FALSE |  |  |  |  | Controlled Load L3 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L4 | FALSE |  |  |  |  | Controlled Load L4 | FALSE |  |  |  |  | Controlled Load L4 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Arm Setting | [5 empty] | Arm Setting | [5 empty] | Arm Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Group ID Setting | [5 empty] | Group ID Setting | [5 empty] | Group ID Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Maintenance Cycle | [5 empty] | Breaker Maintenance Cycle | [5 empty] | Breaker Maintenance Cycle
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Maintenance Hour | 24 |  |  |  |  | Breaker Maintenance Hour | 24 |  |  |  |  | Breaker Maintenance Hour | 24
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Maintenance Randomisation (Minutes) | 2 |  |  |  |  | Breaker Maintenance Randomisation (Minutes) | 2 |  |  |  |  | Breaker Maintenance Randomisation (Minutes) | 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect | [5 empty] | Auto Disconnect | [5 empty] | Auto Disconnect
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load - General | [5 empty] | Controlled Load - General | [5 empty] | Controlled Load - General
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | [5 empty] | Prepayment | [5 empty] | Prepayment
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Back End Communication | [5 empty] | Back End Communication | [5 empty] | Back End Communication
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem | Not configured |  |  |  |  | Modem | Not configured |  |  |  |  | Modem | Not configured
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Settings | [5 empty] | Event Settings | [5 empty] | Event Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event | Setting |  |  |  |  | Event | Setting |  |  |  |  | Event | Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A mains voltage loss | Log Only |  |  |  |  | Phase A mains voltage loss | Log Only |  |  |  |  | Phase A mains voltage loss | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A mains voltage restored | Log Only |  |  |  |  | Phase A mains voltage restored | Log Only |  |  |  |  | Phase A mains voltage restored | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B mains voltage loss | Log Only |  |  |  |  | Phase B mains voltage loss | Log Only |  |  |  |  | Phase B mains voltage loss | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B mains voltage restored | Log Only |  |  |  |  | Phase B mains voltage restored | Log Only |  |  |  |  | Phase B mains voltage restored | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C mains voltage loss | Log Only |  |  |  |  | Phase C mains voltage loss | Log Only |  |  |  |  | Phase C mains voltage loss | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C mains voltage restored | Log Only |  |  |  |  | Phase C mains voltage restored | Log Only |  |  |  |  | Phase C mains voltage restored | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold IV breach start | Log Only |  |  |  |  | QOS threshold IV breach start | Log Only |  |  |  |  | QOS threshold IV breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold IV breach end | Log Only |  |  |  |  | QOS threshold IV breach end | Log Only |  |  |  |  | QOS threshold IV breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold V breach start | Log Only |  |  |  |  | QOS threshold V breach start | Log Only |  |  |  |  | QOS threshold V breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold V breach end | Log Only |  |  |  |  | QOS threshold V breach end | Log Only |  |  |  |  | QOS threshold V breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold VI breach start | Log Only |  |  |  |  | QOS threshold VI breach start | Log Only |  |  |  |  | QOS threshold VI breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold VI breach end | Log Only |  |  |  |  | QOS threshold VI breach end | Log Only |  |  |  |  | QOS threshold VI breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A export energy detected start | Log Only |  |  |  |  | Phase A export energy detected start | Log Only |  |  |  |  | Phase A export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A export energy detected end | Log Only |  |  |  |  | Phase A export energy detected end | Log Only |  |  |  |  | Phase A export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B export energy detected start | Log Only |  |  |  |  | Phase B export energy detected start | Log Only |  |  |  |  | Phase B export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B export energy detected end | Log Only |  |  |  |  | Phase B export energy detected end | Log Only |  |  |  |  | Phase B export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C export energy detected start | Log Only |  |  |  |  | Phase C export energy detected start | Log Only |  |  |  |  | Phase C export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C export energy detected end | Log Only |  |  |  |  | Phase C export energy detected end | Log Only |  |  |  |  | Phase C export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Controlled Load override for LC3 and LC4 | Log Only |  |  |  |  | Extended Controlled Load override for LC3 and LC4 | Log Only |  |  |  |  | Extended Controlled Load override for LC3 and LC4 | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Ripple | Log Only |  |  |  |  | Ripple | Log Only |  |  |  |  | Ripple | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase Rotation | Disabled |  |  |  |  | Phase Rotation | Disabled |  |  |  |  | Phase Rotation | Disabled
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Operation Fail | Log Only |  |  |  |  | Breaker Operation Fail | Log Only |  |  |  |  | Breaker Operation Fail | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker State Mismatch | Log Only |  |  |  |  | Breaker State Mismatch | Log Only |  |  |  |  | Breaker State Mismatch | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Pulse Output Threshold Control | Log Only |  |  |  |  | Pulse Output Threshold Control | Log Only |  |  |  |  | Pulse Output Threshold Control | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multifunction Outputs | [5 empty] | Multifunction Outputs | [5 empty] | Multifunction Outputs

## U3400-31ML3
1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | U3400 Configuration Developer | [5 empty] | U3400 Configuration Developer | [5 empty] | U3400 Configuration Developer
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Identification | [5 empty] | Identification | [5 empty] | Identification
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Program File ID | 31MLCC1-001 |  |  |  |  | Program File ID | 31MLCC1-003 |  |  |  |  | Program File ID | 31MLCA1-003
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TimeZone | [5 empty] | TimeZone | [5 empty] | TimeZone
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney |  |  |  |  | Time Zone | (UTC+10:00) Canberra, Melbourne, Sydney
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Options | [5 empty] | Options | [5 empty] | Options
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE |  |  |  |  | Reset Password Lockout On Power Fail | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE |  |  |  |  | Enable Optical Priority | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE |  |  |  |  | Use Crystal for Time Keeping | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering |  |  |  |  | Metering Type | Net Metering
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Total Metering | Total Phase A+B+C |  |  |  |  | Total Metering | Total Phase A+B+C |  |  |  |  | Total Metering | Total Phase A+B+C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0 |  |  |  |  | Tamper Event Grace Period (minutes) | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Memory | Extended 1 |  |  |  |  | Memory | Extended 1 |  |  |  |  | Memory | Extended 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Registers | [5 empty] | Registers | [5 empty] | Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | [5 empty] | Number of Rates | [5 empty] | Number of Rates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of Rates | 1 |  |  |  |  | Number of Rates | 1 |  |  |  |  | Number of Rates | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Registers | [5 empty] | Energy Registers | [5 empty] | Energy Registers
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register | Description |  |  |  |  | Register | Description |  |  |  |  | Register | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 1 | kWh Imported Total |  |  |  |  | Register 1 | kWh Imported Total |  |  |  |  | Register 1 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 2 | kWh Exported Total |  |  |  |  | Register 2 | kWh Exported Total |  |  |  |  | Register 2 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 3 | kVARh Imported Total(Q1+Q2) |  |  |  |  | Register 3 | kVARh Imported Total(Q1+Q2) |  |  |  |  | Register 3 | kVARh Imported Total(Q1+Q2)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 4 | kVARh Exported Total(Q3+Q4) |  |  |  |  | Register 4 | kVARh Exported Total(Q3+Q4) |  |  |  |  | Register 4 | kVARh Exported Total(Q3+Q4)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 5 | kWh Imported Phase A |  |  |  |  | Register 5 | kWh Imported Phase A |  |  |  |  | Register 5 | kWh Imported Phase A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Register 6 | kWh Imported Phase B |  |  |  |  | Register 6 | kWh Imported Phase B |  |  |  |  | Register 6 | kWh Imported Phase B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels | [5 empty] | Export Wh Warning Levels
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Description | Value |  |  |  |  | Description | Value |  |  |  |  | Description | Value
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Phase A | 0 |  |  |  |  | Phase A | 0 |  |  |  |  | Phase A | 240
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Phase B | 0 |  |  |  |  | Phase B | 0 |  |  |  |  | Phase B | 240
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Phase C | 0 |  |  |  |  | Phase C | 0 |  |  |  |  | Phase C | 240
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Demand | [5 empty] | Demand | [5 empty] | Demand
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero. | [5 empty] | Number of demand registers is zero.
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOU Settings | [5 empty] | TOU Settings | [5 empty] | TOU Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Times | [5 empty] | Switch Times | [5 empty] | Switch Times
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate |  |  | Season No. | Day Type | Time | Rate
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Recurring Dates | [5 empty] | Recurring Dates | [5 empty] | Recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read | Month | Day | Offset | Day Of Week | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-recurring Dates | [5 empty] | Non-recurring Dates | [5 empty] | Non-recurring Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read |  |  |  | Date | Action | Prev Period Read
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Configuration | [5 empty] | Load Profile Configuration | [5 empty] | Load Profile Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1 |  |  |  |  | Number Of Groups | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description |  |  |  |  | LP Group 1 | Load Profile Channel Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | kWh Imported Total |  |  |  |  | Channel 1 | kWh Imported Total |  |  |  |  | Channel 1 | kWh Imported Total
FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Channel 2 | kWh Exported Total |  |  |  |  | Channel 2 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min |  |  |  |  | Interval minutes | 5 Min
TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | Storage Days | 401 |  |  |  |  | Storage Days | 401 |  |  |  |  | Storage Days | 796
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration | [5 empty] | Quality of Supply Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events | QoS Group | Description | Breach Time (Seconds) | Min | Max | Max Events
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 1 | Voltage Phase A | 60 | 207 | 259 | 100 | Channel 1 | Voltage Phase A | 60 | 207 | 259 | 100 | Channel 1 | Voltage Phase A | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 2 | Voltage Phase B | 60 | 207 | 259 | 100 | Channel 2 | Voltage Phase B | 60 | 207 | 259 | 100 | Channel 2 | Voltage Phase B | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 3 | Voltage Phase C | 60 | 207 | 259 | 100 | Channel 3 | Voltage Phase C | 60 | 207 | 259 | 100 | Channel 3 | Voltage Phase C | 60 | 207 | 259 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 4 | Current Phase A | 60 | -40 | 100 | 100 | Channel 4 | Current Phase A | 60 | -40 | 100 | 100 | Channel 4 | Current Phase A | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 5 | Current Phase B | 60 | -40 | 100 | 100 | Channel 5 | Current Phase B | 60 | -40 | 100 | 100 | Channel 5 | Current Phase B | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Channel 6 | Current Phase C | 60 | -40 | 100 | 100 | Channel 6 | Current Phase C | 60 | -40 | 100 | 100 | Channel 6 | Current Phase C | 60 | -40 | 100 | 100
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Settings | [5 empty] | Display Settings | [5 empty] | Display Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1 |  |  |  |  | Energy Decimal Places | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE |  |  |  |  | Suppress Leading Zeroes | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | No. of Energy Digits | 7 |  |  |  |  | No. of Energy Digits | 7 |  |  |  |  | No. of Energy Digits | 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display Groups | [5 empty] | Display Groups | [5 empty] | Display Groups
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Display List | [5 empty] | Normal Display List | [5 empty] | Normal Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss) |  |  |  |  | 1 | Time(hh:mm ss)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Date |  |  |  |  | 2 | Date |  |  |  |  | 2 | Date
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | kWh Imported Total |  |  |  |  | 3 | kWh Imported Total |  |  |  |  | 3 | kWh Imported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total |  |  |  |  | 5 | kWh Exported Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 88 | Display Test |  |  |  |  | 88 | Display Test |  |  |  |  | 88 | Display Test
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 1 Display List | [5 empty] | Alternative 1 Display List | [5 empty] | Alternative 1 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7 |  |  |  |  | 20 | Serial No First 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7 |  |  |  |  | 21 | Serial No Mid 7
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision |  |  |  |  | 22 | Firmware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 23 | Program File ID |  |  |  |  | 23 | Program File ID |  |  |  |  | 23 | Program File ID
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 24 | Program File Version |  |  |  |  | 24 | Program File Version |  |  |  |  | 24 | Program File Version
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision |  |  |  |  | 25 | Hardware Revision
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status |  |  |  |  | 26 | Standard Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status |  |  |  |  | 27 | Manufacturer Meter Status
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining |  |  |  |  | 28 | Estimated % Battery Life Remaining
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alternative 2 Display List | [5 empty] | Alternative 2 Display List | [5 empty] | Alternative 2 Display List
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5 | [5 empty] | Scroll Time [Secs] 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Display ID | Description |  |  |  |  | Display ID | Description |  |  |  |  | Display ID | Description
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1 | Voltage Phase A |  |  |  |  | 1 | Voltage Phase A |  |  |  |  | 1 | Voltage Phase A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 2 | Amps Phase A |  |  |  |  | 2 | Amps Phase A |  |  |  |  | 2 | Amps Phase A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 3 | Voltage Phase B |  |  |  |  | 3 | Voltage Phase B |  |  |  |  | 3 | Voltage Phase B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 4 | Amps Phase B |  |  |  |  | 4 | Amps Phase B |  |  |  |  | 4 | Amps Phase B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 5 | Voltage Phase C |  |  |  |  | 5 | Voltage Phase C |  |  |  |  | 5 | Voltage Phase C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 6 | Amps Phase C |  |  |  |  | 6 | Amps Phase C |  |  |  |  | 6 | Amps Phase C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7 | Power Factor Total |  |  |  |  | 7 | Power Factor Total |  |  |  |  | 7 | Power Factor Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 8 | Frequency |  |  |  |  | 8 | Frequency |  |  |  |  | 8 | Frequency
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 9 | Power Active Total |  |  |  |  | 9 | Power Active Total |  |  |  |  | 9 | Power Active Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 10 | Power Reactive Total |  |  |  |  | 10 | Power Reactive Total |  |  |  |  | 10 | Power Reactive Total
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Settings | [5 empty] | Relay Settings | [5 empty] | Relay Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting | [5 empty] | Relay Present Mask Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker | TRUE |  |  |  |  | Breaker | TRUE |  |  |  |  | Breaker | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 | TRUE |  |  |  |  | Controlled Load L1 | TRUE |  |  |  |  | Controlled Load L1 | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE |  |  |  |  | Controlled Load L2 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L3 | FALSE |  |  |  |  | Controlled Load L3 | FALSE |  |  |  |  | Controlled Load L3 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L4 | FALSE |  |  |  |  | Controlled Load L4 | FALSE |  |  |  |  | Controlled Load L4 | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Arm Setting | [5 empty] | Arm Setting | [5 empty] | Arm Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE |  |  |  |  | Connect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE |  |  |  |  | Disconnect Arm | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up |  |  |  |  | Randomisation Method | On Power Up
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout | [5 empty] | Breaker Arming Timeout
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours |  |  |  |  | Timeout | 1 Hours
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Group ID Setting | [5 empty] | Group ID Setting | [5 empty] | Group ID Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20 |  |  |  |  | Primary Group ID | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200 |  |  |  |  | Secondary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200 |  |  |  |  | Tertiary Group ID | 200
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Maintenance Cycle | [5 empty] | Breaker Maintenance Cycle | [5 empty] | Breaker Maintenance Cycle
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Maintenance Hour | 24 |  |  |  |  | Breaker Maintenance Hour | 24 |  |  |  |  | Breaker Maintenance Hour | 24
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Maintenance Randomisation (Minutes) | 2 |  |  |  |  | Breaker Maintenance Randomisation (Minutes) | 2 |  |  |  |  | Breaker Maintenance Randomisation (Minutes) | 2
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control | [5 empty] | Normal Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0 |  |  |  |  | Normal Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1 |  |  |  |  | Normal Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0 |  |  |  |  | Normal Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30 |  |  |  |  | Normal Supply Reclose Delay [minutes] | 30
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control | [5 empty] | Emergency Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5 |  |  |  |  | Emergency Demand Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0 |  |  |  |  | Emergency Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15 |  |  |  |  | Emergency Supply Reclose Delay [minutes] | 15
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control | [5 empty] | TOD Import Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1 |  |  |  |  | Import Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0 |  |  |  |  | Import Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control | [5 empty] | TOD Export Supply Capacity Control
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00 |  |  |  |  | Monitoring Start Time [HH:MM] | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5 |  |  |  |  | Monitoring Duration [minutes] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1 |  |  |  |  | Export Demand Duration [trading intervals] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0 |  |  |  |  | Export Demand Limit [kW] | 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1 |  |  |  |  | Reclose Delay [minutes] | 1
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings | [5 empty] | Supply Capacity Control Initial Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE |  |  |  |  | Enable Normal SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE |  |  |  |  | Enable Emergency SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE |  |  |  |  | Enable TodImport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE |  |  |  |  | Enable TodExport SCC | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect | [5 empty] | Auto Disconnect | [5 empty] | Auto Disconnect
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5 |  |  |  |  | Auto Disconnect Monitoring Period [seconds] | 5
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20 |  |  |  |  | Auto Disconnect Demand Limit [W] | 20
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3 |  |  |  |  | Auto Disconnect Breach Time [seconds] | 3
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply | [5 empty] | Breaker Loss of Supply
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE |  |  |  |  | Enable Loss of Supply | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load - General | [5 empty] | Controlled Load - General | [5 empty] | Controlled Load - General
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE |  |  |  |  | Ignore time table delay on power up | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 Functionalities | [5 empty] | Controlled Load L1 Functionalities | [5 empty] | Controlled Load L1 Functionalities
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Loss of Supply | [5 empty] | Loss of Supply | [5 empty] | Loss of Supply
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Loss of Supply | FALSE |  |  |  |  | Support Loss of Supply | FALSE |  |  |  |  | Support Loss of Supply | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Power Restore | [5 empty] | Power Restore | [5 empty] | Power Restore
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Power Restore | FALSE |  |  |  |  | Support Power Restore | FALSE |  |  |  |  | Support Power Restore | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Priority Override | [5 empty] | Priority Override | [5 empty] | Priority Override
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Priority Override | TRUE |  |  |  |  | Support Priority Override | TRUE |  |  |  |  | Support Priority Override | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Override Period (HH:MM) | 8:00 |  |  |  |  | Override Period (HH:MM) | 8:00 |  |  |  |  | Override Period (HH:MM) | 8:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Random Delay (HH:MM) | 0:00 | 0:00 |  |  |  | Random Delay (HH:MM) | 0:00 | 0:00 |  |  |  | Random Delay (HH:MM) | 0:00 | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost | [5 empty] | Boost | [5 empty] | Boost
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Boost | TRUE |  |  |  |  | Support Boost | TRUE |  |  |  |  | Support Boost | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost Duration | 8 hours |  |  |  |  | Boost Duration | 8 hours |  |  |  |  | Boost Duration | 8 hours
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Allow to stop boost by pressing boost button | TRUE |  |  |  |  | Allow to stop boost by pressing boost button | TRUE |  |  |  |  | Allow to stop boost by pressing boost button | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Stop boost when ESCC is enabled | TRUE |  |  |  |  | Stop boost when ESCC is enabled | TRUE |  |  |  |  | Stop boost when ESCC is enabled | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost Energy Redirection | Phase C |  |  |  |  | Boost Energy Redirection | Phase C |  |  |  |  | Boost Energy Redirection | Phase C
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost Primacy Initial Command | [5 empty] | Boost Primacy Initial Command | [5 empty] | Boost Primacy Initial Command
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable Boost Primacy | TRUE |  |  |  |  | Enable Boost Primacy | TRUE |  |  |  |  | Enable Boost Primacy | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Under Frequency Load Control (UFLC) | [5 empty] | Under Frequency Load Control (UFLC) | [5 empty] | Under Frequency Load Control (UFLC)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Under Frequency Load Control | FALSE |  |  |  |  | Support Under Frequency Load Control | FALSE |  |  |  |  | Support Under Frequency Load Control | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Demand Limiting Load Control (DLLC) | [5 empty] | Demand Limiting Load Control (DLLC) | [5 empty] | Demand Limiting Load Control (DLLC)
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Demand Limiting Load Control | FALSE |  |  |  |  | Support Demand Limiting Load Control | FALSE |  |  |  |  | Support Demand Limiting Load Control | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Table | [5 empty] | Time Table | [5 empty] | Time Table
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Time Table | TRUE |  |  |  |  | Support Time Table | TRUE |  |  |  |  | Support Time Table | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | General Settings | [5 empty] | General Settings | [5 empty] | General Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Random Delay (HH:MM) | 0:00 | 0:30 |  |  |  | Random Delay (HH:MM) | 0:00 | 0:30 |  |  |  | Random Delay (HH:MM) | 0:00 | 0:30
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Default Relay Action | Open |  |  |  |  | Default Relay Action | Open |  |  |  |  | Default Relay Action | Open
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cycler Configuration | [5 empty] | Cycler Configuration | [5 empty] | Cycler Configuration
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cycler Type | Standard |  |  |  |  | Cycler Type | Standard |  |  |  |  | Cycler Type | Standard
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum |  |  |  |  | Minimum | Maximum
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Initial Delay(T1) | 0:00 | 0:00 |  |  |  | Initial Delay(T1) | 0:00 | 0:00 |  |  |  | Initial Delay(T1) | 0:00 | 0:00
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Close Duration(T2) | 0:01 |  |  |  |  | Close Duration(T2) | 0:01 |  |  |  |  | Close Duration(T2) | 0:01
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Open Duration(T3) | 0:01 |  |  |  |  | Open Duration(T3) | 0:01 |  |  |  |  | Open Duration(T3) | 0:01
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season Switch Dates | [5 empty] | Season Switch Dates | [5 empty] | Season Switch Dates
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Month | Day | Offset | Day Of Week | Action |  | Month | Day | Offset | Day Of Week | Action |  | Month | Day | Offset | Day Of Week | Action
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | January | 1 | No Offset |  | Season Change 0 |  | January | 1 | No Offset |  | Season Change 0 |  | January | 1 | No Offset |  | Season Change 0
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season 0 Normal Scheduler | [5 empty] | Season 0 Normal Scheduler | [5 empty] | Season 0 Normal Scheduler
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Table A | [5 empty] | Switch Table A | [5 empty] | Switch Table A
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Time | Action |  |  |  |  | Switch Time | Action |  |  |  |  | Switch Time | Action
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 7:00 | Instant Open |  |  |  |  | 7:00 | Instant Open |  |  |  |  | 7:00 | Instant Open
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 23:00 | Delayed Close |  |  |  |  | 23:00 | Delayed Close |  |  |  |  | 23:00 | Delayed Close
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Applies to | [5 empty] | Applies to | [5 empty] | Applies to
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Monday | [5 empty] | Monday | [5 empty] | Monday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tuesday | [5 empty] | Tuesday | [5 empty] | Tuesday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Wednesday | [5 empty] | Wednesday | [5 empty] | Wednesday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thursday | [5 empty] | Thursday | [5 empty] | Thursday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Friday | [5 empty] | Friday | [5 empty] | Friday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Saturday | [5 empty] | Saturday | [5 empty] | Saturday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Sunday | [5 empty] | Sunday | [5 empty] | Sunday
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Table B | [5 empty] | Switch Table B | [5 empty] | Switch Table B
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Switch Time | Action |  |  |  |  | Switch Time | Action |  |  |  |  | Switch Time | Action
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Applies to | [5 empty] | Applies to | [5 empty] | Applies to
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Ripple | [5 empty] | Ripple | [5 empty] | Ripple
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Ripple Control | FALSE |  |  |  |  | Support Ripple Control | FALSE |  |  |  |  | Support Ripple Control | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | [5 empty] | Prepayment | [5 empty] | Prepayment
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE |  |  |  |  | Support Prepayment | FALSE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Back End Communication | [5 empty] | Back End Communication | [5 empty] | Back End Communication
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem | Not configured |  |  |  |  | Modem | Not configured |  |  |  |  | Modem | Not configured
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None |  |  |  |  | Modem Reset Type | None
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Settings | [5 empty] | Event Settings | [5 empty] | Event Settings
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event | Setting |  |  |  |  | Event | Setting |  |  |  |  | Event | Setting
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only |  |  |  |  | Primary Power Down | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only |  |  |  |  | Primary Power Up | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only |  |  |  |  | Time Changed (old time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only |  |  |  |  | Time Changed (new time used as time stamp) | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only |  |  |  |  | Procedure Invoked | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only |  |  |  |  | Table Written To | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only |  |  |  |  | Reset List Pointers | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only |  |  |  |  | Event Log Cleared | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only |  |  |  |  | Season Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only |  |  |  |  | Special Schedule Activated | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only |  |  |  |  | Self check error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only |  |  |  |  | Non-volatile memory failure detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only |  |  |  |  | Measurement error detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only |  |  |  |  | Low battery detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only |  |  |  |  | Tamper attempt detected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A mains voltage loss | Log Only |  |  |  |  | Phase A mains voltage loss | Log Only |  |  |  |  | Phase A mains voltage loss | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A mains voltage restored | Log Only |  |  |  |  | Phase A mains voltage restored | Log Only |  |  |  |  | Phase A mains voltage restored | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B mains voltage loss | Log Only |  |  |  |  | Phase B mains voltage loss | Log Only |  |  |  |  | Phase B mains voltage loss | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B mains voltage restored | Log Only |  |  |  |  | Phase B mains voltage restored | Log Only |  |  |  |  | Phase B mains voltage restored | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C mains voltage loss | Log Only |  |  |  |  | Phase C mains voltage loss | Log Only |  |  |  |  | Phase C mains voltage loss | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C mains voltage restored | Log Only |  |  |  |  | Phase C mains voltage restored | Log Only |  |  |  |  | Phase C mains voltage restored | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only |  |  |  |  | QOS threshold I breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only |  |  |  |  | QOS threshold I breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only |  |  |  |  | QOS threshold II breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only |  |  |  |  | QOS threshold II breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only |  |  |  |  | QOS threshold III breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only |  |  |  |  | QOS threshold III breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold IV breach start | Log Only |  |  |  |  | QOS threshold IV breach start | Log Only |  |  |  |  | QOS threshold IV breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold IV breach end | Log Only |  |  |  |  | QOS threshold IV breach end | Log Only |  |  |  |  | QOS threshold IV breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold V breach start | Log Only |  |  |  |  | QOS threshold V breach start | Log Only |  |  |  |  | QOS threshold V breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold V breach end | Log Only |  |  |  |  | QOS threshold V breach end | Log Only |  |  |  |  | QOS threshold V breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold VI breach start | Log Only |  |  |  |  | QOS threshold VI breach start | Log Only |  |  |  |  | QOS threshold VI breach start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | QOS threshold VI breach end | Log Only |  |  |  |  | QOS threshold VI breach end | Log Only |  |  |  |  | QOS threshold VI breach end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A export energy detected start | Log Only |  |  |  |  | Phase A export energy detected start | Log Only |  |  |  |  | Phase A export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase A export energy detected end | Log Only |  |  |  |  | Phase A export energy detected end | Log Only |  |  |  |  | Phase A export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B export energy detected start | Log Only |  |  |  |  | Phase B export energy detected start | Log Only |  |  |  |  | Phase B export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase B export energy detected end | Log Only |  |  |  |  | Phase B export energy detected end | Log Only |  |  |  |  | Phase B export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C export energy detected start | Log Only |  |  |  |  | Phase C export energy detected start | Log Only |  |  |  |  | Phase C export energy detected start | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase C export energy detected end | Log Only |  |  |  |  | Phase C export energy detected end | Log Only |  |  |  |  | Phase C export energy detected end | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only |  |  |  |  | Service Disconnect open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only |  |  |  |  | Service Disconnect close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only |  |  |  |  | Service Disconnect armed for open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only |  |  |  |  | Service Disconnect armed for close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only |  |  |  |  | Controlled Load L1 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only |  |  |  |  | Controlled Load L1 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only |  |  |  |  | Controlled Load L2 open | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only |  |  |  |  | Controlled Load L2 close | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only |  |  |  |  | Primary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only |  |  |  |  | Primary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only |  |  |  |  | Secondary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only |  |  |  |  | Secondary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only |  |  |  |  | Tertiary group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only |  |  |  |  | Tertiary group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm |  |  |  |  | Service Disconnect open due to auto-disconnect | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm |  |  |  |  | Service Disconnect open due to supply capacity | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm |  |  |  |  | Service Disconnect close after supply capacity timeout. | Alarm
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only |  |  |  |  | Controlled Load override. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only |  |  |  |  | Multiple events logged today | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only |  |  |  |  | Controlled Load override timer expired. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Controlled Load override for LC3 and LC4 | Log Only |  |  |  |  | Extended Controlled Load override for LC3 and LC4 | Log Only |  |  |  |  | Extended Controlled Load override for LC3 and LC4 | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only |  |  |  |  | Controlled Load closed due to boost. | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only |  |  |  |  | Reprogramming | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only |  |  |  |  | Scroll button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only |  |  |  |  | Alt button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only |  |  |  |  | Boost button pressed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only |  |  |  |  | Service Disconnect close acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only |  |  |  |  | Service Disconnect open acknowledged | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only |  |  |  |  | Primary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only |  |  |  |  | Secondary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only |  |  |  |  | Tertiary group command table write | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only |  |  |  |  | Failed password on login | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only |  |  |  |  | Multiple failed logins | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only |  |  |  |  | Communication lockout | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only |  |  |  |  | Firmware changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only |  |  |  |  | Master group command accepted | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only |  |  |  |  | Master group command rejected | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only |  |  |  |  | Local Parameter Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only |  |  |  |  | Remote Power Fail | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only |  |  |  |  | Communications Update | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only |  |  |  |  | Load Profile Status Change | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only |  |  |  |  | Multi Source Tamper | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only |  |  |  |  | Extended Load Control | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Ripple | Log Only |  |  |  |  | Ripple | Log Only |  |  |  |  | Ripple | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only |  |  |  |  | Critical Table Changed | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phase Rotation | Disabled |  |  |  |  | Phase Rotation | Disabled |  |  |  |  | Phase Rotation | Disabled
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker Operation Fail | Log Only |  |  |  |  | Breaker Operation Fail | Log Only |  |  |  |  | Breaker Operation Fail | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only |  |  |  |  | Prepayment | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker State Mismatch | Log Only |  |  |  |  | Breaker State Mismatch | Log Only |  |  |  |  | Breaker State Mismatch | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only |  |  |  |  | Breaker LOS | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Pulse Output Threshold Control | Log Only |  |  |  |  | Pulse Output Threshold Control | Log Only |  |  |  |  | Pulse Output Threshold Control | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only |  |  |  |  | Extended Event | Log Only
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Multifunction Outputs | [5 empty] | Multifunction Outputs | [5 empty] | Multifunction Outputs