Communication Networks

# Communication Networks

# TEST CERTIFICATE

Document control:

| Certificate Name | Functional Acceptance Testing for: Meter Program 0C1 for 10ML3, 10ML4, 10ML5 L&G meters running R6.4 |
| --- | --- |
| Certificate Number: | Program 10ML3, 10ML4_0C1_R64_Ver_2 |
| Version No. | 1.0 |
| Created on | Tuesday, 24 March 2026Right click on date , select Update Field to revise date |
| Last Updated | Tuesday, 24 March 2026Right click on date , select Update Field to revise date Right click on date , select Update Field to revise date |
| Status: | FinalDraft Highlight as appropriate |

| Approval Status |  |  |  |  |
| --- | --- | --- | --- | --- |
| Test Certificate Approved |  |  | Date |  |
| Stake Holder Title | Stakeholder Name | Approval Signature |  | Date |
| Senior Metering Engineer | Fabian Perez | Insert hyperlink to approval |  |  |
| Asset Engineer (Distribution Intelligence) | Hansi Rajapaksha Vithanage Dona |  |  |  |

Business in Confidence

Document Details

| Roles | Name |
| --- | --- |
| Document Owner | Leonard Jarillas |
| Document Administrator | Manoj Kalra |

Document purpose

The purpose of this Communication Network Technology Test Certificate is to document the outcomes and recommendations found whilst testing L&G meter program 0C1, Version 2, for 10ML3, 10ML4, 10ML5 meters running firmware R6.4.

change control

- The Document Owner will approve changes to this test certificate document

- The Document Administrator will be responsible for communicating changes to the wider business

Document Review

| Reviewer Title | Reviewer Name | Review Yes/No |
| --- | --- | --- |
| Communication Networks Laboratory Technician | Kamau Njuguna | Yes |

CONTENTS

1	sUMMARY	1

2	INTRODUCTION	1

2.1	Background	1

2.2	Motivation for testing	1

3	TEST DETAILS	2

3.1	Testing methodology	2

3.2	Details of combination tested	3

3.3	Test Results Overview	3

3.4	Test Results Summary	4

4	Recommendation	4

Issues and Deployment notes	5

4.1	Issues Found	5

4.2	Deployment Notes	5

5	REvision History	6

# sUMMARY

Meter programs are responsible for defining the settings within a meter. These settings affect the function of the meter and how it records metering data. A meter program for L&G 10ML3, 10ML4 and 10ML5 meters has been developed to allow the recording of both import and export energy. This program is named “0C1”.

Prior to the remote deployment of program 0C1, for 10ML3, 10ML4 and 10ML5 meters into the production AMI system it is deemed important to ensure that this meter program poses no risk to the business. To achieve this, the Communication Networks Quality group carried out testing to ensure correct functionality (see section 3.4 for details).

Testing for the remote deployment of L&G meter program 0C1 for 10ML3, 10ML4 and 10ML5 meters running R6.4 firmware is complete. It was carried out with the configuration detailed in section 3 “Details of the Combination Tested”.

It is recommended that meter “program 0C1 for 10ML3, 10ML4 and 10ML5 meters” can be remotely deployed within the AMI Network with minimal risk to the business.

# INTRODUCTION

## Background

All meters within the AMI network can be re-configured to function differently depending on the requirements of the installation. This reconfiguration is done through meter programs. When a meter is first delivered, it comes pre-configured with a particular meter program. Which meter program is used for a particular site is usually decided based on whether it contains solar electricity, electric hot water or slab heating.

Over time particular meter program needs to be changed to better service latest metering requirements. This program update can be achieved remotely, without the need for a site visit or the replacement of the meter.

Specifically the following settings can be changed in a meter program:

- Interval data channels

- Energy Registers

- Quality of supply / Supply capacity thresholds

- LCD display settings

- Load control switching times

- Event log recording, the events are unified across U1300 programs.

## Motivation for testing

Version 2 of 10ML_0C1_R64 program is created to accommodate U1300 10ML meters running R6.4 meter firmware. 10ML_0C1_R64 meter program is based on U1300_10ML3_0C1_v001 meter program apart from that the changes due to moving to the new version of EMPWin version 6.7.10. The 10ML3_0C1_R64 meter program is exactly the same but has been saved and exported using the newer version of EMPWin.

# TEST DETAILS

## Testing methodology

The testing of meter programs is focused on the recording and collection of metering data. Specifically the following aspects are covered:

- Compatibility of the new program to R6.4 firmware.

- Programming of meters remotely from one deployed version to another, using the version of MPC currently operating in the production AMI environment.

- Verification of meter settings by comparing the original meter program with that read out of the meter after programming.

- Meter program audits can verify the presence of the program on a given meter.

- Interval, register and event data are checked from end to end, this verifies that:

  - The meter is recording the correct channels and registers.

  - All metering data including events are being collected remotely by the AMI system.

  - The data recorded on the meter is identical to that read out of UIQ

- Supply contactor responds to remote connect and disconnect commands

- Changes in the program made on top of current prod version are verified.

Note: The Test program for R64 meter FW was tested successfully and later the Test program was updated for the Broadcast Group ID values (Primary Group ID- 20, Secondary Group ID- 200 and Tertiary Group ID- 200). After the modification, it was verified that the original Tested Program and the modified program are same except the value for Primary Group, Secondary Group and Tertiary Group ID. So, the program attached to this document and uploaded to the UIQ is the modified Test Program.

## Details of combination tested

The following table details the AMI System Configuration that was used for testing:

| AMI System Configuration Tested |  |
| --- | --- |
| CHED Meter Codes | 10ML3, 10ML4, 10ML5 |
| Meter Firmware versions | R6.4 |
| NIC Hardware Version | NIC320 |
| NIC Firmware Version | 5.4.3 |
| AP Hardware Version | AP 5 |
| AP Firmware Version | 5.4.6043 |
| Environments | DEV |
| AMM Version | Version: 5.0.14-REV13 |
| MPC Version | Version: 4.16.7 build 2000715 |
| Meter Program name | 0C1 |
| Meter program version | 2 |
| Meter program file name | U1300_10ML3_0C1_v002_R64.xml |

## Test Results Overview

| Name of Test Plans | U1300_10ML3_0C1_v002_R64 |
| --- | --- |
| Test Period | 14/01/2025 – 24/01/2025 |
| Test Location | AMI Technology Laboratory CitiPower Powercor 7 Cahir Court, Brooklyn, VIC 3012 |
| Number of test cases | 8 |
| Test cases blocked | 0 |
| Test cases that failed | 0 |
| Tests cases that partially passed | 0 |
| Tests cases that passed | 8 |

## Test Results Summary

| Test group | Result | Business risk |
| --- | --- | --- |
| Program Settings | Pass | None |
| Audit meter program | Pass | None |
| Meter Setting before programming | Pass | None |
| Meter programming | Pass | None |
| Supply contactor operation | Pass | None |
| LCD Information | RBT | None |
| Meter Program Data Integrity | Pass | None |
| Meter Tamper | RBT | None |

# Recommendation

L&G meter program 0C1, Version 2, for 10ML3, 10ML4 and 10ML5 meters for R6.4 firmware, has been tested under the configuration detailed in section 3 “Details of the Combination Tested”.

Communication Network Technology recommends that L&G meter program 0C1, Version 2, for 10ML3, 10ML4 and 10ML5 meters can be deployed on AMI meters in the field with R6.4 firmware with minimal risk to the business.

# Issues and Deployment notes

## Issues Found

None.

## Deployment Notes

### This program will erase all accumulated and interval data. Any data that is needed should be read of the meter before reprogramming.

### This program will erase all existing configurations in the meter (i.e. ESCC settings). The values for these configurations should be set again after full programming.

### This program is only for U1300 L&G single phase meters without load contactor (10ML3, 10ML4 and 10ML5 meter code)

### Meters should first be running NIC firmware 5.4.3. Meters should be running meter firmware R6.4. MPC will produce and error similar to the following if the firmware is incorrect

“Meter fw_version_string 'S00237-05.05.R27' does not match programming script 'S00244-08.02.R64'”

### The meter program was only tested on 10ML3 (U1300 Version 1) meter. Even if this is the case, this does not pose any risk based on historical meter program test results wherein hardware version 1 and 2 of U1300 have the same firmware and accepts the same program.

### Meter events settings are similar to the 11ML3 and 12ML3 meters. It is expected that no events will be generated by the meter due to the hardware necessary for the event not present (i.e. second element, load contactor). If there are any unexpected events generated, this should immediately be reported to the Communications Quality group.

### The program file is attached below.

### When the meter program is uploaded to MPC it should produce the same seal, size and checksum as below (verifying it is the same program):

# REvision History

| Date | Revised By | Notes |
| --- | --- | --- |
| 13/01/2025 | Manoj Kalra | Initial Draft |
| 16/04/2025 | Manoj Kalra | Final |